## Details
Sr.N | Site ID | New NSS ID | DG/Non DG | Zone | Global ID | Site Name | Cluster | IME | CE | RCA-1 | RCA-2 | Action Plan | Status | Closure Date/TAT | Jan-25 | Feb-25 | Mar-25 | Apr-25 | 2025 PD Count
1 | PWNR01 | IDMH100129 | DG | ID_CHANDRAPUR | 451431 | POWANPUR | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Controller faulty | Controller replaced | Reopen | 2025-03-31 |  | 0.5 |  | 2 | 2
2 | PLAM01 | IDMH101191 | DG | ID_NANDED | 505086 | PALAM | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | BB | BB Backup Very Low | BB replaced | Closed | 2025-02-12 | 11 | 4 |  |  | 2
3 | NGPR77 | IDMH101405 | DG | ID_NAGPUR | 458084 | RAJIV NAGAR | NAGPUR | SAI | KAILASH POKALE | BB | Low Battery Backup | BB replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
4 | KKAD01 | IDMH109139 | DG | ID_AHMEDNAGAR | 528029 | KAKADI | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS RM Faulty | RM replaced | Closed | 2025-01-22 | 1 |  |  |  | 1
5 | AMVT52 | IDMH109888 | NON DG | ID_AMRAVATI | 572727 | SBI COLONY | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
6 | PU1137 | IDMH110391 | NON DG | ID_PUNENORTH | 574919 | VINAYAK NAGAR | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
7 | BHAT01 | IDMH102584 | DG | ID_AMRAVATI | 565838 | BHATKULI | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
8 | TLDG01 | IDMH104881 | DG | ID_AHMEDNAGAR | 460096 | TALEGAON DIGHE | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
9 | KOL197 | INMH406354 | NON DG | ID_KOLHAPUR | 595372 | Koundusakar_Petrol_Pump | KOLHAPUR | SSS | RITESH RANGOLE | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
10 | AMVT92 | INMH406929 | NON DG | ID_AMRAVATI | 451561 | CAMPROAD_DMART_VF | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS BER | OD SMPS required with BB Cabinet | Open | 2025-05-07 | 8 | 7 | 6.5 | 4 | 4
11 | AUR164 | IDMH109767 | DG | ID_AURANGABAD | 524972 | BEED BY PASS | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
12 | SIRD06 | IDMH107755 | DG | ID_AHMEDNAGAR | 460033 | 2000 ROOMS SHIRDI_COW | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS Backplane faulty | Plan For Smps Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
13 | PAJ582 | INMH408269 | NON DG | ID_GOA | 451578 | SEAVIEWAPTT_VF | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS to DCDB voltage drop > 3.6 & SMPS Controller Faulty | ATC to replace Cable & SMPS Controller rectification Plan | Open | 2025-05-22 | 0.5 |  |  |  | 1
14 | AMVT43 | IDMH108296 | DG | ID_AMRAVATI | 531385 | UTTAM NAGAR_2 | AKOLA | SAI | BHUSHAN BAREKAR | BB | BB cell faulty | BB replaced | Closed | 2025-02-15 | 2.5 |  |  |  | 1
15 | AMBA01 | IDMH101422 | DG | ID_AMRAVATI | 507086 | AMBADA | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
16 | UDGR05 | IDMH101845 | DG | ID_SOLAPUR | 459512 | REDDY COLONY | LATUR | SAI | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
17 | SIKS01 | IDMH103035 | DG | ID_AHMEDNAGAR | 464927 | SHIRUR KASAR | LATUR | PTPL | ASHWIN KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
18 | WRDH29 | IDMH112242 | DG | ID_NAGPUR | 565956 | WARDHA RLY STATION | NAGPUR | SAI | VIVEK GANJARE | RRU | 1 RRU Faulty | RRU replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
19 | AURN32 | IDMH103639 | DG | ID_AURANGABAD | 459890 | WALUJ GAON | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | SMPS Backplane faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
20 | RATN11 | IDMH108156 | DG | ID_KOLHAPUR | 566926 | MERIA BANDAR | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD Faulty | Plan for rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
21 | HARE01 | IDMH104172 | DG | ID_AHMEDNAGAR | 507075 | HAREGAON | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
22 | CHLI04 | IDMH102189 | NON DG | ID_AKOLA | 458407 | RAUTWADI, BULDHANA | AKOLA | SAI | RANJEET KAPSE | SMPS | smps controllar faulty | SMPS rectification done | Closed | 2025-03-10 | 2.5 | 0.5 | 1 |  | 3
23 | PUN900 | IDMH106348 | DG | ID_PUNESOUTH | 521806 | SUS ROAD | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
24 | YAVT18 | IDMH100172 | DG | ID_AMRAVATI | 565995 | OPEN PLOT.YAVATMAL. | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
25 | CHLI07 | IDMH100216 | DG | ID_AKOLA | 565792 | SHIVAJI PARK_CHIKHALI_BULDHANA | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Load sharing issue | load correction done | Closed | 2025-03-31 | 1 | 0.5 |  |  | 2
26 | AKOT05 | IDMH100335 | DG | ID_AKOLA | 458064 | GAZI PLOT | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
27 | WKHD01 | IDMH100787 | DG | ID_AKOLA | 458264 | WANKHED | AKOLA | SAI | RANJEET KAPSE | BB | BB Backup very low | Plan for BB upgradation | Closed | 2025-03-31 | 0.5 |  |  |  | 1
28 | SGPR01 | IDMH101083 | DG | ID_AKOLA | 565336 | SANGRAMPUR | AKOLA | SAI | RANJEET KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
29 | AKLA24 | IDMH101111 | DG | ID_AKOLA | 505145 | HOTEL JASNAGARA (STN. RD. AKOLA) | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
30 | PUSD02 | IDMH101120 | DG | ID_AMRAVATI | 460298 | PUSAD ENGINEERING COLLEGE | AKOLA | SAI | DHANRAJ NIBALKAR | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 | 1 |  | 2
31 | DAAD01 | IDMH101269 | DG | ID_AKOLA | 458603 | DHAD | AKOLA | SAI | RANJEET KAPSE | SMPS | Smps Lvd Faulty | Plan for SMPS rectification | Closed | 2025-03-31 | 0.5 | 0.5 |  |  | 2
32 | WSHM01 | IDMH101548 | DG | ID_AMRAVATI | 460366 | RATHIS PLOT | AKOLA | SAI | ALI SHAH | SMPS | SMPS issue | SMPS replaced | Closed | 2025-03-31 | 1.5 |  |  |  | 1
33 | DMPI01 | IDMH101895 | DG | ID_AHMEDNAGAR | 459724 | DHARMAPURI | LATUR | PTPL | ASHWIN KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 5 | 1
34 | DHAN01 | IDMH102095 | DG | ID_AKOLA | 458175 | DHANORA | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
35 | PMSA01 | IDMH102838 | DG | ID_AKOLA | 505454 | PIMPALGAON SARAI | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-04-09 | 0.5 |  | 0.5 | 3 | 3
36 | WWND01 | IDMH103433 | DG | ID_AKOLA | 458438 | WARWAND | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 | 0.5 |  | 2
37 | SRNI01 | IDMH102544 | DG | ID_AHMEDNAGAR | 459673 | SARNI | LATUR | PTPL | ASHWIN KAPSE | SMPS | Smps Lvd Faulty | Rectification Pending | Open | 2025-04-30 | 0.5 |  |  |  | 1
38 | KLWD01 | IDMH103957 | DG | ID_AHMEDNAGAR | 460258 | KOLPEWADI | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
39 | AMBD03 | IDMH102733 | DG | ID_AURANGABAD | 531026 | AMBAD - JALNA | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | SMPS | SMPS Backplane faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
40 | BBWR01 | IDMH103958 | NON DG | ID_AHMEDNAGAR | 505288 | BABHLESHWAR | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-04-24 |  | 1 |  |  | 1
41 | NIGO01 | IDMH104548 | DG | ID_AHMEDNAGAR | 459888 | NIGHOJ | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB cell faulty | BB replaced | Closed | 2025-04-24 |  | 0.5 |  |  | 1
42 | KRJI01 | IDMH105515 | DG | ID_AHMEDNAGAR | 460119 | KARANJI BK | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
43 | PRLA01 | IDMH103031 | DG | ID_AKOLA | 458048 | PAROLA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | OK/BER | Plan for replacement | Open | 2025-05-30 |  |  | 0.5 |  | 1
44 | WRDH28 | IDMH107556 | DG | ID_NAGPUR | 505172 | MEDICAL COLLEGE | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS controller Faulty | SMPS rectification done | Closed | 2025-04-09 | 0.5 |  | 0.5 | 1 | 3
45 | LHAR01 | IDMH108417 | DG | ID_AMRAVATI | 523960 | LOHARA_NEW | AKOLA | SAI | ALI SHAH | SMPS | SMPS Controller & LVD Faulty | LVD and BLVD Correction done. 45 and42 and Delta SMPS Rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
46 | TWLI01 | IDMH110067 | DG | ID_AMRAVATI | 523906 | TIWALI | AKOLA | SAI | ALI SHAH | BB | Zero Battery backup | Need to replace aging BB | Open | 2025-05-15 | 1 | 0.5 |  |  | 2
47 | ADUL01 | IDMH104099 | DG | ID_AURANGABAD | 460041 | ADUL | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
48 | AKLA64 | IDMH110716 | DG | ID_AKOLA | 565818 | OLD TARFILE AKOLA | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-12 | 2.5 | 4.5 | 5 |  | 3
49 | NGP377 | IDMH111041 | DG | ID_NAGPUR | 565469 | SAI NAGAR | NAGPUR | SAI | MILIND RAMTEKE | RRU | RRU Faulty | RRU rectification req | Open | VIL Support Required |  | 0.5 | 0.5 |  | 2
50 | LONI02 | IDMH111731 | DG | ID_AHMEDNAGAR | 460309 | HASNAPUR | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-05-22 | 1.5 |  |  |  | 1
51 | DOTN01 | IDMH104301 | DG | ID_AHMEDNAGAR | 459496 | DEODAITHAN | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS BER | Power plant required | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
52 | NGP342 | IDMH112244 | DG | ID_NAGPUR | 531031 | JANKI NAGAR | NAGPUR | SAI | MILIND RAMTEKE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 | 1 | 1 | 3 | 7 | 4
53 | PUN998 | IDMH109030 | DG | ID_PUNENORTH | 566627 | PIMPRI VILLAGE- JAMTANI BUILDING | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
54 | NGP715 | INMH405777 | NON DG | ID_NAGPUR | 592985 | Satgaon_Airtel | NAGPUR | SAI | VIVEK GANJARE | RRU | 1 RRU Faulty | RRU replaced | Closed | 2025-01-31 | 0.5 |  |  |  | 1
55 | WRDH46 | INMH405920 | DG | ID_NAGPUR | 565734 | WARDHA INDUSTRIAL AREA | NAGPUR | SAI | VIVEK GANJARE | RRU | 1 RRU Faulty | RRU replaced | Closed | 2025-01-31 | 0.5 |  |  |  | 1
56 | PUN331 | IDMH105355 | DG | ID_PUNESOUTH | 459088 | SHINDE ALI | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
57 | AKJG01 | IDMH101008 | DG | ID_AKOLA | 458018 | AKOLI JAHANGIR | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-05-15 | 1 |  | 1.5 |  | 2
58 | JMGN01 | IDMH101509 | DG | ID_AMRAVATI | 458060 | JAMGAON | AKOLA | SAI | BHUSHAN BAREKAR | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
59 | HRAL01 | IDMH101594 | DG | ID_AMRAVATI | 460118 | HARAL | AKOLA | SAI | ALI SHAH | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
60 | AKLA20 | IDMH101697 | DG | ID_AKOLA | 458289 | WASHIM BYPASS | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
61 | AKOT07 | IDMH101851 | NON DG | ID_AKOLA | 505516 | AKOT BUS STAND- AKOT FI | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 1.5 |  |  | 1
62 | MKPR01 | IDMH102749 | DG | ID_AKOLA | 458045 | MALKAPUR | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Backplane faulty | Plan for Rectification | Open | 2025-04-30 |  | 1 |  | 5 | 2
63 | MTLA02 | IDMH110120 | NON DG | ID_AKOLA | 565730 | MOTALA | AKOLA | SAI | RANJEET KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
64 | CHGN02 | IDMH106883 | DG | ID_AURANGABAD | 458541 | GHAT ROAD_CHGN02_COW | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | Smps Lvd Faulty | Rectification Pending | Open | 2025-04-20 | 1.5 |  | 1 |  | 2
65 | POKH01 | IDMH101768 | DG | ID_AKOLA | 520905 | POPATKHED | AKOLA | SAI | Vacant CE Akola | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
66 | LXMD01 | IDMH103194 | DG | ID_SATARA | 458956 | LAXMI DAHIWADI | SOLAPUR | SAI | CHANDRAKANT ANGADI | Cable | SMPS to DCDB Underated cable & Voltage drop > 3 V | cable to replace | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
67 | MALI01 | IDMH103588 | DG | ID_SATARA | 459533 | MALINAGAR | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-16 | 0.5 | 1 | 0.5 |  | 3
68 | PAJ179 | IDMH107275 | NON DG | ID_GOA | 461359 | RIVIERA DE | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
69 | HGLI08 | IDMH100171 | DG | ID_NANDED | 566189 | AZAM COLONY | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 |  |  | 1
70 | AKLA19 | IDMH100388 | DG | ID_AKOLA | 458300 | AKOLA ENGG. COLLEGE (BABULGAON) | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
71 | NSK122 | IDMH108107 | DG | ID_NASHIK | 571576 | ANANDWALI-3 | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS faulty | SMPS replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
72 | AMVT47 | IDMH108450 | DG | ID_AMRAVATI | 531382 | UJWAL COLONY | AKOLA | SAI | BHUSHAN BAREKAR | RRU | RRU Faulty | Support req | Open | VIL Support Required |  | 1 | 0.5 | 2 | 3
73 | PDKV02 | IDMH108509 | DG | ID_CHANDRAPUR | 505544 | PANDHARKAWDA_4 | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
74 | TLHR01 | IDMH100988 | DG | ID_AKOLA | 458172 | TELHARA | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
75 | PUSD03 | IDMH101065 | DG | ID_AMRAVATI | 460256 | PUSAD II | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
76 | PDPN01 | IDMH109689 | DG | ID_CHANDRAPUR | 567121 | PANDARPOUNI RPTR | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 1 |  |  | 1
77 | MHUR01 | IDMH101170 | DG | ID_NANDED | 460375 | MAHUR | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-20 | 1.5 |  | 1 |  | 2
78 | AMVT01 | IDMH101423 | DG | ID_AMRAVATI | 458279 | SHYAM THEATER-AMVT01 | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Controller Faulty | Plan for rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
79 | SATE01 | IDMH101480 | DG | ID_AMRAVATI | 458080 | SATEGAON | AKOLA | SAI | BHUSHAN BAREKAR | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 |  |  |  | 1
80 | PU1296 | IDMH110139 | NON DG | ID_PUNESOUTH | 577369 | NEAR COSMOS RESIDENC | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
81 | KOLP20 | INMH404765 | DG | ID_KOLHAPUR | 459819 | JARAGNAGAR | KOLHAPUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  |  | 1
82 | NGP405 | IDMH110977 | NON DG | ID_NAGPUR | 500299 | HUDKESHWAR-2 | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS BER | Replacement Pending | Open | 2025-05-15 | 1 | 1.5 |  |  | 2
83 | RATN42 | INMH406080 | NON DG | ID_KOLHAPUR | 566933 | RATNAGIRI MIDC | KOLHAPUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
84 | YAVT12 | IDMH101508 | DG | ID_AMRAVATI | 500183 | BHOSA ROAD ,YAVATMAL | AKOLA | SAI | DHANRAJ NIBALKAR | BB | Low Battery backup | bbdt work Done | Reopen | 2025-03-10 |  | 0.5 |  | 1 | 2
85 | WNJA01 | IDMH101516 | DG | ID_AMRAVATI | 458606 | WANOJA | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 | 0.5 | 1 | 3
86 | MZRI01 | IDMH101570 | DG | ID_AMRAVATI | 458168 | MOZARI | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
87 | KTUL01 | IDMH111616 | DG | ID_NASHIK | 458013 | KAHATUL | NASHIK | ATS | NILESH BHAVSAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
88 | MLBZ01 | IDMH101659 | DG | ID_AKOLA | 458223 | MALEGAON BAZAR | AKOLA | SAI | Vacant CE Akola | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
89 | ISLI01 | IDMH101910 | DG | ID_AKOLA | 458398 | ISOLI | AKOLA | SAI | RANJEET KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
90 | KBWR01 | IDMH102366 | DG | ID_AKOLA | 458433 | KALAMBESHWAR | AKOLA | SAI | RANJEET KAPSE | SMPS | RM Faulty | RM replaced | Reopen | 2025-03-31 | 0.5 | 1 |  | 1 | 3
91 | ROHA05 | IDMH112202 | DG | ID_RAIGARH | 570452 | ROHA | PUNE-2 | ATS | AMAY DORUGADE | Load Segregation | Backup 1 hrs,RM issue last 2 month, RM add,&load balancing required in DCDB both Baseband critical to non critical connection pending only | RM add, DCDB both Baseband critical to non critical connection done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
92 | AKLA93 | INMH003293 | NON DG | ID_AKOLA | 505222 | AKOT FILE | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
93 | CHLI01 | IDMH103740 | DG | ID_AKOLA | 458408 | CHIKLI01 | AKOLA | SAI | RANJEET KAPSE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 |  |  | 1
94 | AKLA44 | IDMH108357 | DG | ID_AKOLA | 571559 | PANCHASHIL NAGAR_AKOLA | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
95 | MALE02 | IDMH108358 | DG | ID_AMRAVATI | 502264 | MALEGAON 2 | AKOLA | SAI | ALI SHAH | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
96 | LONI09 | INMH006114 | DG | ID_AHMEDNAGAR | 566865 | LONI PRAVARA | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-20 | 1 | 0.5 |  |  | 2
97 | LNVL26 | INMH400920 |  | ID_RAIGARH | 530265 | HUDCO COLONY_LONAVALA | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | Smps Controller Faulty | SMPS Rectififiaction done | Closed | 2025-04-09 | 1.5 |  | 1.5 | 3 | 3
98 | AKLA53 | IDMH109252 | NON DG | ID_AKOLA | 576972 | KHOLESHWAR | AKOLA | SAI | Vacant CE Akola | SMPS | smps controllar faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
99 | SHGN05 | IDMH109507 | DG | ID_AKOLA | 531546 | SANT GAJANAN ENGG | AKOLA | SAI | RANJEET KAPSE | SMPS | RM faulty | RM replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
100 | NGPR76 | INMH404549 | NON DG | ID_NAGPUR | 458362 | AIRPORT | NAGPUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
101 | AKLA62 | IDMH110770 | DG | ID_AKOLA | 574908 | CHOTI UMRI | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
102 | MKPR05 | IDMH111456 | DG | ID_AKOLA | 507124 | OLD CITY (MALKAPUR) | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Backplane faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 0.5 | 2 | 2
103 | LONR02 | IDMH112215 | DG | ID_AKOLA | 565806 | LONAR 2 | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | Support req | Open | VIL Support Required |  | 1 | 2 |  | 2
104 | YAVT28 | IDMH112219 | DG | ID_AMRAVATI | 565994 | AMBER LAWN | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
105 | KHOR01 | INMH002716 | DG | ID_AKOLA | 458423 | KHOR | AKOLA | SAI | RANJEET KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
106 | PU2262 | INMH407979 | NON DG | ID_PUNENORTH | 451536 | AMANORA_TWR25_VF | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS To DCDB Cable drop > 6 V & SMPS Obsolute model | Plan for Cable replacement & New SMPS Req | Open | 2025-05-15 | 3 |  | 0.5 | 1 | 3
107 | KAHR01 | IDMH102978 | DG | ID_SATARA | 459627 | KANHER | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS LVD Faulty & AC Faulty | SMPS replaced | Closed | 2025-04-24 | 1 |  |  |  | 1
108 | AMV126 | INMH405769 | NON DG | ID_AMRAVATI | 593950 | Lalkhedi | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  |  | 1
109 | PU1007 | IDMH108767 | NON DG | ID_PUNESOUTH | 532347 | NANO SPACE | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | Plan for SMPS Replacement | Open | 2025-05-30 |  | 1 |  |  | 1
110 | SHDA12 | INMH408459 | DG | ID_NASHIK | 502068 | SHAHADA 5 | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS BER | SMPS replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
111 | CHPD05 | IDMH108388 | DG | ID_AKOLA | 566068 | CHOPA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Cable | DCDB TO RRU voltage drop > 3 | VIL replace cable | Open | VIL Support Required |  | 1 |  | 1 | 2
112 | ARAG01 | IDMH101950 | DG | ID_KOLHAPUR | 459795 | ARAG | KOLHAPUR | SSS | VIVEK DESHPANDE | BB | BB Backup 10 Min & All RRU cable connected with Critical | Changed to Non Critical & New BB Required | Open | 2025-05-30 | 0.5 |  |  |  | 1
113 | AMNR04 | IDMH103709 | DG | ID_AKOLA | 503658 | NR COTTON MARKET - AMALNER | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  | 0.5 | 0.5 |  | 2
114 | TGOD01 | IDMH106751 | DG | ID_NASHIK | 566985 | THENGODA RPT | NASHIK | ATS | Vacant Vacant CE Nashik | Cable | Voltage drop > 3 V | SMPS & BB Replaced & VIL To Replace Cable | Open | VIL Support Required | 1.5 | 0.5 |  | 1 | 3
115 | PU2684 | INMH405537 | NON DG | ID_PUNESOUTH | 590562 | Kamthe Nagar | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS Faulty | SMPS rectification done | Reopen | 2025-03-31 | 3.5 |  | 0.5 | 2 | 3
116 | NLWD01 | IDMH101601 | DG | ID_NAGPUR | 505460 | NALWADI | NAGPUR | SAI | VIVEK GANJARE | RRU | RRU faulty | RRU rectification done | Closed | 2025-04-09 | 0.5 |  |  | 2 | 2
117 | PU2213 | INMH407702 | DG | ID_PUNESOUTH | 566492 | PADMASHALI BHAVAN | PUNE-2 | ATS | RAHUL TUPARE | Cable | SMPS to IP55 Cable AL & 4 v Dropping | VIL to rectify cable 50 sqmm | Open | VIL Support Required | 1 | 0.5 |  |  | 2
118 | ASTI03 | INMH407518 | NON DG | ID_AHMEDNAGAR | 528485 | ASHTI_NEW | AHMEDNAGAR | INHOUSE | DNYANESHWAR POTHARE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
119 | RSHN01 | IDMH102452 | DG | ID_AHMEDNAGAR | 459504 | RASHIN | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | Low battery backup/10min | BB Replaced | Closed | 2025-02-15 | 1.5 |  |  |  | 1
120 | TVSH01 | IDMH104408 | DG | ID_SATARA | 458844 | TAVASHI | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-04-09 | 0.5 |  |  | 1 | 2
121 | MLDG01 | IDMH108331 | DG | ID_AHMEDNAGAR | 523981 | MALWADGN_NEW | AHMEDNAGAR | PTPL | SANDEEP WANI | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1.5 |  |  | 1
122 | PAJ633 | INMH400020 | NON DG | ID_GOA | 451377 | GOASECRETARIAT_VF | GOA | SSS | SURAJ PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 6 | 1
123 | WRNA01 | IDMH103697 | DG | ID_KOLHAPUR | 459696 | WARNANAGAR | KOLHAPUR | SSS | SANTOSH JADHAV | Cable | SMPS to Power BOX on Tower TOP Voltage drop > 3.5 V | VIL to replace cable | Open | VIL Support Required | 1 | 1.5 |  |  | 2
124 | NAND13 | IDMH101019 | DG | ID_NANDED | 460382 | WAJEGAON | LATUR | PTPL | RAJKUMAR ALANE | Load Segregation | Baseband is in critical | Basaband now in NON CRTICAL | Closed | 2025-04-09 | 0.5 | 0.5 |  | 1 | 3
125 | WRDH18 | IDMH106317 | DG | ID_NAGPUR | 505363 | GAJANAN NAGAR | NAGPUR | SAI | VIVEK GANJARE | Load Segregation | VIL Baseband faulty | Rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
126 | JBBR01 | IDMH101024 | DG | ID_AMRAVATI | 460151 | JAMB BAZAR | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS Controller Faulty | SMPS rectification done | Closed | 2025-04-24 | 1 |  | 1 |  | 2
127 | BNGN01 | IDMH102621 | DG | ID_AHMEDNAGAR | 459612 | BHANGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | BB Low Backup & SMPS Faulty | BB & SMPS Replaced | Closed | 2025-01-03 | 0.5 |  |  |  | 1
128 | MODA01 | IDMH100618 | DG | ID_NAGPUR | 458021 | MAUDA | NAGPUR | SAI | MILIND RAMTEKE | RRU | RRU Faulty | RRU rectification req | Open | VIL Support Required |  |  | 0.5 |  | 1
129 | AAST01 | IDMH102499 | DG | ID_SOLAPUR | 459576 | ASHTI | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-16 | 1 | 0.5 | 0.5 |  | 3
130 | PAJM84 | IDMH104123 | DG | ID_GOA | 461447 | CHINCHINIM | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Controller faulty | SMPS replaced | Closed | 2025-04-24 | 4.5 |  |  |  | 1
131 | LAHN01 | IDMH100114 | DG | ID_NANDED | 460166 | LAHAN | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS Obsolute model | Plan for SMPS replacement | Open | 2025-05-07 | 1.5 | 0.5 | 3.5 | 2 | 4
132 | ANGR07 | IDMH103152 | DG | ID_AHMEDNAGAR | 460388 | BHINGARGAON | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | zero backup site | BB upgradation done | Closed | 2025-05-15 | 2 | 0.5 |  |  | 2
133 | GUNW01 | IDMH104723 | DG | ID_PUNESOUTH | 458943 | GUNWADI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 | 2 |  |  |  | 1
134 | VSOL01 | IDMH104211 | DG | ID_NASHIK | 458458 | VASOL | NASHIK | ATS | Vacant Vacant CE Nashik | BB | Rivaval BB,2 Cell Faulty | 2 Cell Rplacement Require | Open | 2025-05-30 |  | 3.5 |  |  | 1
135 | KOGN01 | IDMH105866 | DG | ID_AHMEDNAGAR | 459558 | KOLGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS BER | SMPS Required | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
136 | UMRG01 | IDMH102758 | DG | ID_SOLAPUR | 459539 | UMERGA | SOLAPUR | SAI | ROHIT GHOLAP | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
137 | RADE01 | IDMH102878 | DG | ID_SATARA | 459297 | RADDE | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
138 | ROHA08 | INMH001971 | NON DG | ID_RAIGARH | 507061 | ROHA TOWN | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 4 | 1 | 3 | 4
139 | KLNA01 | IDMH100365 | DG | ID_CHANDRAPUR | 451489 | KOTHARI (KALMANA) | NAGPUR | SAI | GANESH DANDALWAR | BB | BB -cell faulty | BB cell replaced | Reopen | 2025-03-31 | 2 |  |  | 1 | 2
140 | PU1530 | IDMH103542 | NON DG | ID_PUNESOUTH | 465882 | CUMMINS COMPANY | PUNE-2 | ATS | AKSHAY SHELAR | BB | Battery backup 30 min | Plan For new BB replacement | Open | 2025-05-30 |  |  | 0.5 |  | 1
141 | PU2220 | INMH408375 | DG | ID_PUNENORTH | 521156 | AWHALWADI | PUNE-1 | ATS | HARSHAL MAHAJAN | SMPS | SMPS Controller faulty & BB Bbackup 10 min | SMPS Rectifcation & new BB req | Open | 2025-04-30 | 1 | 0.5 |  | 3 | 3
142 | NDGN01 | IDMH104942 | DG | ID_NASHIK | 458414 | NANDGAON | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
143 | PAJ310 | IDMH106625 | NON DG | ID_GOA | 461364 | NITYA RESORT | GOA | SSS | SURAJ PATIL | BB | BB Backup Very Low | BB upgradation done | Closed | 2025-04-24 |  | 1 |  | 2 | 2
144 | MHDE01 | IDMH104418 | NON DG | ID_NASHIK | 458012 | MOHIDA | NASHIK | ATS | NILESH BHAVSAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
145 | LNKD02 | IDMH112150 | DG | ID_NASHIK | 565978 | LONKHEDA | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
146 | NSK112 | IDMH106858 | DG | ID_NASHIK | 459946 | UNTWADI | NASHIK | ATS | SUBHASH SHINDE | SMPS | LVD Bypass | Rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
147 | PU2632 | INMH405539 | NON DG | ID_PUNENORTH | 586513 | Kalptaru Estate_Airtel | PUNE-3 | ATS | Vacant CE Pune-3 | Cable | Voltage Drop aluminium cable( SMPS to DCDB ) | Plan for Replacement | Open | 2025-04-20 |  | 0.5 | 1.5 |  | 2
148 | PAJ116 | IDMH111748 | DG | ID_GOA | 566550 | HONDA | GOA | SSS | SURAJ PATIL | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 1 |  |  | 2
149 | PUN800 | IDMH105816 | NON DG | ID_PUNENORTH | 464908 | EON-B | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | 2013 BB & Zero Backup | Plan for BB upgradation | Open | 2025-05-07 | 2 | 1 | 0.5 |  | 3
150 | TMBT01 | IDMH106496 | DG | ID_RAIGARH | 459609 | TAMBATI-RAIGAD RPT | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS BER | SMPS Installed | Reopen | 2025-01-30 | 0.5 |  |  | 3 | 2
151 | PUNE71 | IDMH106519 | DG | ID_RAIGARH | 458725 | DEHU ROAD (RL) | PUNE-3 | ATS | PRATIK HULAVALE | Cable | SMPS to RRU VLTG Drop >3v | Cable replaced | Closed | 2025-03-16 |  | 0.5 | 0.5 |  | 2
152 | AWPR01 | IDMH100598 | DG | ID_CHANDRAPUR | 459979 | AWARPUR | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
153 | YRML01 | IDMH102805 | DG | ID_SOLAPUR | 459567 | YERMALA | SOLAPUR | SAI | ROHIT GHOLAP | Cable | DCDB to RRU Underrated cable vtg drop 3v | Cable replacement req | Open | VIL Support Required | 1 |  |  |  | 1
154 | CNDA01 | IDMH103328 | DG | ID_AHMEDNAGAR | 460047 | CHANDA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | BB replaced | Closed | 2025-01-10 | 0.5 |  |  |  | 1
155 | TKPR01 | IDMH103464 | DG | ID_AURANGABAD | 458466 | TAKLI PR. | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Cable | BB Backup 15 min & 3-RRU Connected with critical & DCDB TO RRU voltage drop > 4.5 | ATC to replace BB & New DCDB req for non critical & VIL to replace cable | Open | 2025-04-20 | 1 | 1.5 |  |  | 2
156 | RGAR04 | IDMH105102 | DG | ID_PUNENORTH | 459493 | RAJGURUNAGAR | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB cell faulty | Plan for BB Cell Replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
157 | HINJ45 | IDMH111981 | DG | ID_PUNESOUTH | 523090 | TAJ VIVANTA | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
158 | NAND75 | IDMH101305 | DG | ID_NANDED | 465837 | NEAR HOTEL CHANDRALOK | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 |  | 2 | 2
159 | HINJ28 | IDMH105009 | DG | ID_PUNESOUTH | 567017 | OPEN PLOT, HINJEWADI II | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 1 |  |  | 2
160 | AKLA13 | IDMH100675 | DG | ID_AKOLA | 458292 | MURTIZAPUR ROAD, | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
161 | WORA02 | IDMH107199 | DG | ID_CHANDRAPUR | 565396 | WARORA | NAGPUR | SAI | GANESH DANDALWAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
162 | WSHM05 | IDMH100278 | DG | ID_AMRAVATI | 505340 | WASHIM FILL IN(SHUKRAWAR PETH) | AKOLA | SAI | ALI SHAH | BB | BB Backup 5 Min | BB upgradation done | Closed | 2025-03-31 |  | 0.5 |  |  | 1
163 | MGOA13 | IDMH107592 | DG | ID_RAIGARH | 570436 | PEN BURDI- SALINDE | PUNE-3 | ATS | ANANT TIDKE | Cable | DCDB to RRU Voltage drop > 3 V | VIL To replace cable | Open | VIL Support Required | 6.5 | 6.5 | 7 | 11 | 4
164 | KGVN01 | IDMH105576 | DG | ID_NASHIK | 458391 | KARANJGAVHAN | NASHIK | ATS | SWAPNIL SALWE | BB | Battery backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
165 | LONR01 | IDMH102696 | DG | ID_AKOLA | 460089 | LONAR | AKOLA | SAI | RANJEET KAPSE | Cable | DCDB to RRU Voltage drop > 2.5 | VIL to replace cable | Open | VIL Support Required | 2.5 | 0.5 | 2 | 1 | 4
166 | JIPR01 | IDMH101391 | DG | ID_NANDED | 460300 | JAIPUR | AKOLA | PTPL | ALI SHAH | Cable | SMPS to RRU Voltage drop > 4 | VIL To Replace Cable | Open | VIL Support Required | 2.5 | 1 |  |  | 2
167 | PNVL01 | IDMH105160 | DG | ID_PUNENORTH | 459735 | KURLI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 2 |  | 2
168 | CHLE01 | IDMH103272 | DG | ID_SATARA | 459794 | CHALE | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
169 | PUN896 | IDMH107965 | DG | ID_PUNENORTH | 522091 | GANESH NAGAR PCMC_A | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1.5 |  | 2 | 2
170 | PUN176 | IDMH106138 | DG | ID_PUNENORTH | 458760 | AKURDI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
171 | PUN395 | IDMH106207 | NON DG | ID_PUNENORTH | 458968 | NASHIK PHATA | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
172 | TLGN08 | IDMH106521 | DG | ID_RAIGARH | 459722 | INDORI II | PUNE-3 | ATS | PRATIK HULAVALE | Cable | SMPS to RRU VLTG Drop >3v | Cable replaced | Reopen | 2025-03-31 |  | 0.5 | 1.5 | 1 | 3
173 | PUN412 | IDMH106604 | DG | ID_PUNENORTH | 458800 | CHIKHALIGAON | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
174 | SHDA11 | INMH002248 | DG | ID_NASHIK | 505185 | SHAHADA | NASHIK | ATS | NILESH BHAVSAR | Cable | Voltage from DCDB TO RRU > 4.2 v & SMPS LVD Faulty | VIL to replace Cable & ATC Replace LVD | Open | 2025-04-20 |  | 0.5 | 1 | 1 | 3
175 | KNRJ01 | IDMH100170 | DG | ID_AMRAVATI | 458412 | KINI RAJA | AKOLA | SAI | ALI SHAH | SMPS | SMPS Absolute model & Backup Low & Voltage drop from SMPS to RRU > 4 One single cable serve 3-RRU | SMPS Replacement req & VIL to replace cable | Open | 2025-05-30 | 0.5 |  |  |  | 1
176 | KDKL01 | IDMH106799 | NON DG | ID_RAIGARH | 459615 | KHADKALE | PUNE-3 | ATS | PRATIK HULAVALE | RRU | VIL RRU Faulty | RRU Replacement done | Closed | 2025-02-28 | 1.5 | 1 |  |  | 2
177 | PNVL03 | IDMH106857 | DG | ID_RAIGARH | 459616 | KHODKALA | PUNE-3 | ATS | PRATIK HULAVALE | Cable | SMPS to RRU VLTG Drop >3v | Cable replaced | Reopen | 2025-01-30 | 0.5 |  |  | 3 | 2
178 | PUN808 | IDMH107761 | DG | ID_PUNENORTH | 521209 | MEHETRE WADI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 1 | 0.5 |  | 3
179 | TLGN29 | IDMH110588 | DG | ID_RAIGARH | 528948 | NEAR SARASWATI VIDYA MANDIR -TALEGAON | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-03-12 |  | 2 | 0.5 |  | 2
180 | ANDO01 | IDMH100397 | DG | ID_SOLAPUR | 459655 | ANDHORI | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 |  | 0.5 |  | 2
181 | HINJ43 | IDMH111992 | DG | ID_PUNESOUTH | 532472 | INFOSYS INFOTECH_MANN VILLAGE | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
182 | PU1968 | INMH001694 | DG | ID_PUNENORTH | 521210 | KOYNA ROAD | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 1 |  | 2
183 | BHAN05 | IDMH100507 | DG | ID_CHANDRAPUR | 457985 | CHIKHLA MINES | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 3 | 1
184 | KHMR01 | IDMH100582 | DG | ID_CHANDRAPUR | 505453 | KHAMRI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
185 | PU1671 | INMH400651 | DG | ID_PUNENORTH | 567089 | WAKAD2 | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
186 | PU1818 | INMH407705 | DG | ID_PUNENORTH | 566658 | INDIRA GANDHI BRIDGE - PIMPRI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
187 | WSRI01 | IDMH100877 | DG | ID_CHANDRAPUR | 451441 | WASARI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Controller faulty | Controller replaced | Closed | 2025-03-31 | 1 | 1 |  |  | 2
188 | BLNG01 | IDMH106807 | DG | ID_KOLHAPUR | 505239 | BALINGA | KOLHAPUR | SSS | RITESH RANGOLE | Cable | DCDB to RRH cable drop 3.2 V | VIL to replace cable | Open | VIL Support Required | 0.5 |  |  |  | 1
189 | KADL01 | IDMH103369 | DG | ID_SATARA | 459293 | KADLAS | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS RM faulty | RM replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
190 | BALR01 | IDMH101136 | DG | ID_AKOLA | 458303 | BALAPUR | AKOLA | SAI | Vacant CE Akola | SMPS | Controller Backplane & Lvd Faulty Lvd Card Faulty Back Pain Faulty | Plan for rectification | Open | 2025-04-30 |  |  | 1.5 |  | 1
191 | ADLI01 | IDMH101198 | DG | ID_AMRAVATI | 460023 | ADOLI | AKOLA | SAI | ALI SHAH | SMPS | SMPS Obsolute model | Plan for SMPS rectification | Open | 2025-05-22 |  | 1 |  |  | 1
192 | DYPR03 | IDMH101200 | DG | ID_AMRAVATI | 457975 | MURTIZAPUR ROAD | AKOLA | SAI | BHUSHAN BAREKAR | Cable | RRU To DCDB Voltage drop > 5 V | Additional 1 core cable to add | Open | VIL Support Required | 1 | 1.5 |  |  | 2
193 | RDPR01 | IDMH101244 | DG | ID_AMRAVATI | 505319 | RIDDHAPUR | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Smps Obsulate Model | Replacement Pending | Open | 2025-05-15 |  | 3 | 0.5 | 2 | 3
194 | NSK103 | IDMH107585 | DG | ID_NASHIK | 460304 | DEOLALI CAMP 2 | NASHIK | ATS | SUBHASH SHINDE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | Cable replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
195 | NAND20 | IDMH101378 | DG | ID_NANDED | 505339 | GURUDWARA | LATUR | PTPL | Vacant CE Latur | SMPS | Smps Lvd Faulty | Rectification Pending | Open | 2025-05-22 | 1 |  |  |  | 1
196 | SWNT01 | IDMH107764 | DG | ID_GOA | 461288 | MUNICIPAL BLDG. | GOA | SSS | KISHOR SHIRSATH | Cable | 6sq mm cable used for RRU/3.0v drop DCDB to RRU | VIL to replace cable | Open | VIL Support Required |  | 0.5 |  |  | 1
197 | PU2244 | INMH406853 | DG | ID_PUNESOUTH | 566494 | BHAVANI PETH | PUNE-2 | ATS | RAHUL TUPARE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-15 |  | 0.5 | 0.5 |  | 2
198 | RNUN01 | IDMH101563 | DG | ID_AURANGABAD | 460192 | RANI UNCHEGAON | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-16 | 1 | 1.5 | 1 |  | 3
199 | JAMG01 | IDMH101976 | DG | ID_AURANGABAD | 460155 | JAMGAON | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Load Segregation | RRU Power supply from IP55 MCB & Drop > 2 V & SMPS LVD Faulty | VIL To Shift Power tapping from IP55 TO ATC DCDB & ATC to rectify LVD | Open | 2025-04-20 | 1 | 1 |  |  | 2
200 | TMSA01 | IDMH102025 | DG | ID_NANDED | 460082 | TAMSA | LATUR | PTPL | Vacant CE Latur | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
201 | PRLI01 | IDMH102173 | DG | ID_AHMEDNAGAR | 459445 | PARLI VAIJANATH (1) | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
202 | SYGB01 | IDMH102318 | DG | ID_AHMEDNAGAR | 458862 | SAYGAON | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
203 | PUN483 | IDMH104333 | DG | ID_PUNESOUTH | 459262 | SADASHIV PETH 2 | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
204 | PNST02 | IDMH104452 | DG | ID_PUNESOUTH | 459738 | KHOPI | PUNE-2 | ATS | RAHUL TUPARE | Cable | SMPS to RRU VLTG Drop >3v | cable to replace | Open | VIL Support Required | 1 | 0.5 | 0.5 |  | 3
205 | JAWL01 | IDMH102968 | DG | ID_AHMEDNAGAR | 507080 | JAWLA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | Low battery backup/15min | BB Replaced | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
206 | PRGT01 | IDMH105610 | DG | ID_PUNENORTH | 567011 | PIRANGUTE | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS Controller faulty | SMPS rectification done | Reopen | 2025-02-28 |  | 0.5 |  | 1 | 2
207 | PUN839 | IDMH105706 | DG | ID_PUNESOUTH | 521486 | SANTOSH NAGAR | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 4 | 1
208 | PUNE84 | IDMH106247 | DG | ID_PUNESOUTH | 464884 | KHAMDHENU RIDDHI, SAHAJANAND SOC | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
209 | PUN862 | IDMH112392 | DG | ID_PUNESOUTH | 521887 | SINHAGAD COLLEGE-NARHE TOP | PUNE-2 | ATS | AKSHAY SHELAR | BB | Low Battery backup | BB replaced | Closed | 2025-03-31 | 1 |  |  |  | 1
210 | KURU01 | IDMH104128 | DG | ID_SATARA | 458946 | KURDU | SOLAPUR | SAI | BALASAHEB KADAM | Cable | DCDB to RRU Drop > 3 V | VIL to Replace cable | Open | VIL Support Required | 2 |  |  |  | 1
211 | NGPR90 | IDMH100304 | DG | ID_NAGPUR | 458143 | RAIPUR | NAGPUR | SAI | KAILASH POKALE | RRU | RRU Faulty | RRU replaced | Closed | 2025-01-31 | 0.5 |  |  |  | 1
212 | PAJ366 | INMH001748 | DG | ID_GOA | 451290 | MAPUSAMKT_VF | GOA | SSS | KISHOR SHIRSATH | Cable | 3.6v drop DCDB to RRU/6sq mm cable used for RRU | VIL to replace cable | Open | VIL Support Required |  | 0.5 |  |  | 1
213 | NASK88 | IDMH104515 | DG | ID_NASHIK | 460398 | OZAR MIG | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS Controller & LVD Faulty | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
214 | MPUR01 | IDMH104978 | DG | ID_NASHIK | 458236 | MALPUR | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
215 | SRIM03 | IDMH104986 | DG | ID_AHMEDNAGAR | 566809 | SRIRAMPUR | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB Backup low | BB replaced | Closed | 2025-04-24 | 2 | 0.5 |  |  | 2
216 | EXPH02 | IDMH105539 | DG | ID_RAIGARH | 458721 | SADAWALI | PUNE-3 | ATS | PRATIK HULAVALE | Cable | DCDB to RRU cable long distance 50m | cable distance reduction req | Open | VIL Support Required |  |  | 0.5 |  | 1
217 | NGP313 | IDMH110073 | DG | ID_NAGPUR | 573486 | SWABLAMBI NAGAR | NAGPUR | SAI | KAILASH POKALE | RRU | RRU Faulty | RRU replaced | Closed | 2025-01-31 | 1 |  |  |  | 1
218 | HINJ11 | IDMH105597 | DG | ID_PUNESOUTH | 459033 | HINJEWADI VILLAGE | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 1.5 | 0.5 | 1.5 | 1 | 4
219 | AWBK01 | IDMH105949 | DG | ID_RAIGARH | 460086 | AWASARI | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-15 |  | 0.5 | 1.5 |  | 2
220 | PNVL05 | IDMH106072 | DG | ID_RAIGARH | 459605 | RAJMACHI | PUNE-3 | ATS | PRATIK HULAVALE | Cable | DCDB to RRU Voltage drop > 3.5 V | VIL To replace cable | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
221 | NASK66 | IDMH106174 | NON DG | ID_NASHIK | 459908 | KRANTI NAGAR | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS Controller faulty & BER | Plan for SMPS replacement | Open | 2025-05-15 | 1 | 0.5 |  |  | 2
222 | PUN494 | IDMH106267 | DG | ID_PUNENORTH | 458743 | AJMERA COLONY | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 |  | 0.5 | 0.5 |  | 2
223 | SRWD01 | IDMH106431 | DG | ID_SATARA | 459379 | SUDRUKWADI | KOLHAPUR | SSS | VINOD SAWANT | SMPS | SMPS Calliberation issue | SMPS Calliberation rectified | Closed | 2025-01-30 | 1 |  |  |  | 1
224 | ORAS01 | IDMH105587 | DG | ID_GOA | 464875 | ORAS | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-31 | 0.5 |  | 1 |  | 2
225 | KHRD01 | IDMH103583 | DG | ID_SATARA | 505246 | KHARDI | SOLAPUR | PTPL | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-04-09 |  | 0.5 |  | 1 | 2
226 | PUN443 | IDMH106910 | DG | ID_PUNESOUTH | 459057 | BANER MHALUNGE | PUNE-2 | ATS | VIPIN GUPTA | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 1 |  |  |  | 1
227 | HRTL06 | INMH004537 | DG | ID_KOLHAPUR | 505133 | HATHKANANGLE | KOLHAPUR | SSS | SANTOSH JADHAV | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
228 | NGP225 | IDMH106957 | DG | ID_NAGPUR | 505535 | BESA | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS MCB Faulty | MCB replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
229 | WKSI01 | IDMH101043 | DG | ID_RAIGARH | 522972 | KINARA RESORT | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS controller Faulty | Plan For Smps Rectification | Open | 2025-04-30 | 3.5 |  |  | 2 | 2
230 | LOHA01 | IDMH101419 | DG | ID_NANDED | 507034 | LOHA | LATUR | PTPL | Vacant CE Latur | Load Segregation | RRU to Critical | RRU load circtal to Non circatl work done | Reopen | 2025-03-31 | 1 | 0.5 | 0.5 | 2 | 4
231 | ISPR03 | IDMH103761 | DG | ID_KOLHAPUR | 459551 | MAHADEV NAGAR (ISLAMPUR) | KOLHAPUR | SSS | VINOD SAWANT | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 | 0.5 | 3 | 3
232 | SATR09 | IDMH104236 | DG | ID_SATARA | 458639 | CHIDANAND HTS(RELOCATION) | KOLHAPUR | SSS | VINAYAK KOLEKAR | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
233 | MNDL01 | IDMH104272 | DG | ID_NASHIK | 458233 | MANDAL | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS LVD faulty | SMPS rectification done | Closed | 2025-03-10 | 3 |  | 0.5 |  | 2
234 | PUN876 | IDMH108497 | DG | ID_PUNENORTH | 451279 | NEWDATTANAGAR_VF_HUB | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Load Segregation | 2 RRU at Critical suply | RRU shifted to Non Critical | Closed | 2025-01-30 | 0.5 |  |  |  | 1
235 | WTGN01 | IDMH104900 | DG | ID_KOLHAPUR | 459540 | WATEGAON | KOLHAPUR | SSS | VINOD SAWANT | BB | Low battery backup | Need to replace BB | Open | 2025-05-30 | 0.5 |  |  |  | 1
236 | MLGN21 | IDMH108632 | NON DG | ID_NASHIK | 527503 | HOTEL SUNARA PALACE_NEW | NASHIK | ATS | SWAPNIL SALWE | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-15 | 4 |  |  |  | 1
237 | KHAM12 | IDMH109783 | DG | ID_AKOLA | 527316 | WADI (BHIM NAGAR). | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Controller Faulty & Voltage drop from DCDB to RRU >3 v | SMPS rectification done & cable replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
238 | AMVT71 | IDMH109990 | NON DG | ID_AMRAVATI | 528688 | LALKHADI01 | AKOLA | SAI | BHUSHAN BAREKAR | RRU | RRU Faulty | Support req | Open | VIL Support Required |  |  | 0.5 |  | 1
239 | PUN242 | IDMH105638 | DG | ID_PUNESOUTH | 459462 | ATUR NAGAR | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | SMPS controller rectification Req | Open | 2025-04-20 | 6.5 | 3 | 1.5 | 1 | 4
240 | ARNI03 | IDMH110430 | DG | ID_AMRAVATI | 465482 | ARNI3 | AKOLA | SAI | DHANRAJ NIBALKAR | BB | Zero battery backup | Need to replace BB | Open | 2025-05-15 | 5.5 | 3 |  |  | 2
241 | SVTR01 | IDMH106225 | DG | ID_SATARA | 505485 | SHIVTHAR | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
242 | PAJM06 | IDMH106893 | NON DG | ID_GOA | 460624 | JOSHI BUILDING | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Controller faulty & BB Backup up 10 Min | SMPS rectification & BB replacement done | Closed | 2025-04-24 |  | 0.5 |  |  | 1
243 | BLPT01 | IDMH107127 | DG | ID_RAIGARH | 570213 | BORLI PANCHAYAT | PUNE-2 | ATS | AMAY DORUGADE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-03-16 | 0.5 | 1.5 | 1 |  | 3
244 | FLGN01 | IDMH111310 | DG | ID_AMRAVATI | 451409 | GHARPHAL/ FALEGAON | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS BER | SMPS Replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
245 | ARLL01 | IDMH111322 | DG | ID_CHANDRAPUR | 451358 | ARLI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS LVD Faulty & DCDB to RRU voltage drop 2.5 | SMPS replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
246 | PUN672 | IDMH107762 | DG | ID_PUNENORTH | 507123 | NEHRU NAGAR III | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
247 | NAND46 | IDMH108366 | DG | ID_NANDED | 531350 | LAXMINAGAR | LATUR | PTPL | Vacant CE Latur | BB | Zero Battery Backup | BB replaced | Closed | 2025-04-24 | 0.5 | 0.5 | 0.5 | 2 | 4
248 | PU1080 | IDMH109716 | NON DG | ID_PUNENORTH | 464744 | MAGARPATTA_TWR8_IBS | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
249 | PRLI07 | IDMH111562 | DG | ID_AHMEDNAGAR | 507122 | BAJRANG NAGAR (PARLI 2) | LATUR | PTPL | ASHWIN KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
250 | NAND61 | IDMH110105 | DG | ID_NANDED | 507128 | NEW KAUTHA | LATUR | PTPL | Vacant CE Latur | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 4.5 | 3 | 4.5 | 7 | 4
251 | ITKL01 | IDMH100548 | DG | ID_SOLAPUR | 465829 | ITKAL | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-15 | 2 | 0.5 |  |  | 2
252 | DKSL01 | IDMH100961 | DG | ID_SOLAPUR | 459054 | DIKSAL | SOLAPUR | SAI | ROHIT GHOLAP | Cable | DCDB to RRU Underrated cable vtg drop 3v | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
253 | CHRL02 | IDMH111880 | DG | ID_AMRAVATI | 502770 | CHANDUR RAILWAY 2 | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS Controller Faulty | SMPS rectification done | Closed | 2025-03-31 | 2 |  | 1 |  | 2
254 | KNHE02 | IDMH111912 | DG | ID_RAIGARH | 566995 | KANE PHATA | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | Smps Lvd Faulty | Rectification Pending | Open | 2025-04-30 | 0.5 |  |  |  | 1
255 | ANGR48 | IDMH111953 | NON DG | ID_AHMEDNAGAR | 505392 | HOTEL RUCHIRA | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | Battery backup very low | BB upgradation done | Closed | 2025-04-30 | 0.5 | 0.5 |  |  | 2
256 | KOLP78 | IDMH112022 | DG | ID_KOLHAPUR | 566350 | NH-4,GOKUL SHIRGAON MIDC | KOLHAPUR | SSS | RITESH RANGOLE | BB | BB 6 cell faulty/Backup 15min | BB Cell to be replace | Open | 2025-04-30 |  | 0.5 |  |  | 1
257 | SATR60 | INMH004603 | DG | ID_SATARA | 566527 | SATARA MIDC | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 1 |  |  |  | 1
258 | PU1721 | INMH408405 | NON DG | ID_PUNENORTH | 527983 | THERGAON_IDU | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
259 | ANGR89 | INMH001101 | DG | ID_AHMEDNAGAR | 566025 | VASANT TEKDI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS Faulty | SMPS Replaced | Closed | 2025-01-22 | 0.5 |  |  |  | 1
260 | BTHI01 | IDMH101847 | DG | ID_NANDED | 459871 | BOTHI | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS BER | Replacement Pending | Open | 2025-05-15 | 1.5 |  | 1.5 | 4 | 3
261 | WANI03 | IDMH100359 | DG | ID_CHANDRAPUR | 459876 | WANI MIDC | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS Controller Faulty | SMPS Rectification Done | Closed | 2025-04-24 | 0.5 |  |  | 3 | 2
262 | ISPR02 | IDMH103946 | DG | ID_KOLHAPUR | 459544 | SAKHARALE | KOLHAPUR | SSS | VINOD SAWANT | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
263 | PNST09 | IDMH104130 | DG | ID_SATARA | 459316 | BALEGAR | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
264 | SIND02 | INMH402613 | DG | ID_NAGPUR | 502737 | SINDHI RLY 2 | NAGPUR | SAI | VIVEK GANJARE | Cable | Voltage drop > 3 V | RRU cable underated 6 sqmm need to change by VIL | Open | VIL Support Required | 2 | 0.5 |  | 1 | 3
265 | NGP557 | INMH005705 | NON DG | ID_NAGPUR | 451348 | VHBCOLONY_VF | NAGPUR | INHOUSE | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
266 | PSWL01 | IDMH104340 | DG | ID_SATARA | 458957 | PUSESAVALI | KOLHAPUR | SSS | VINOD SAWANT | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 1.5 |  |  |  | 1
267 | GDUR01 | IDMH103131 | DG | ID_AHMEDNAGAR | 505313 | GHATNANDOOR | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS Faulty & DCDB TO RRU Voltage drop > 4 | New SMPS Required & VIL to replace cable | Open | 2025-04-30 | 1.5 | 1.5 |  |  | 2
268 | KDHR04 | IDMH107202 | DG | ID_NANDED | 531525 | KANDHAR 3 | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Backplane faulty | SMPS replaced | Closed | 2025-02-09 |  | 0.5 |  |  | 1
269 | SSLA01 | IDMH101695 | DG | ID_AHMEDNAGAR | 460048 | SIRSALA | LATUR | PTPL | ASHWIN KAPSE | SMPS | Smps Lvd Faulty | Rectification Pending | Open | 2025-05-22 |  | 3.5 |  |  | 1
270 | MRNG01 | IDMH101535 | DG | ID_NAGPUR | 505283 | KHARANGANA | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS BLVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 1 |  | 1
271 | NKUR01 | IDMH102615 | DG | ID_AHMEDNAGAR | 459498 | NEKNUR | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS Faulty & DCDB TO RRU Voltage drop > 4 | New SMPS Required & VIL to replace cable | Open | 2025-05-15 |  | 0.5 | 1 |  | 2
272 | KDSI01 | IDMH100619 | DG | ID_NAGPUR | 458123 | KHINDSI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU faulty | Support req | Open | VIL Support Required |  | 0.5 |  |  | 1
273 | AUSA02 | IDMH102747 | DG | ID_SOLAPUR | 505106 | AUSAGAON | LATUR | PTPL | SUDHIR AGHE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
274 | MJLG01 | IDMH102748 | DG | ID_AURANGABAD | 460341 | MAJALGAON | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 2 |  |  |  | 1
275 | DUND11 | IDMH100550 | DG | ID_PUNESOUTH | 465838 | DAUND SUGAR FACTORY | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
276 | GKDA02 | IDMH100611 | DG | ID_NANDED | 460265 | DATTA NAGAR (GOKUNDA) | LATUR | PTPL | RAJKUMAR ALANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
277 | NVGK01 | IDMH104125 | DG | ID_KOLHAPUR | 464827 | NIGAVE KHALSA | KOLHAPUR | SSS | RITESH RANGOLE | Cable | cable drop | VIL to Replace Cable | Open | VIL Support Required | 1.5 | 0.5 |  |  | 2
278 | MORC01 | IDMH104350 | DG | ID_SATARA | 459472 | MOROCHI | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-15 | 1 | 1 |  |  | 2
279 | PAJM20 | IDMH104518 | DG | ID_GOA | 461448 | BHUTNATH | GOA | SSS | SUNIL TAMSE | SMPS | controller faulty +controller card faulty | Plan for rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
280 | SDNE01 | IDMH104613 | DG | ID_NASHIK | 458548 | SAUNDANE | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
281 | SHRR01 | IDMH100915 | DG | ID_CHANDRAPUR | 451309 | SHIRPAUR_U | NAGPUR | SAI | GANESH DANDALWAR | RRU | RRU faulty | RRU rectification req | Open | VIL Support Required |  | 0.5 | 2 | 2 | 3
282 | PUN866 | IDMH107516 | DG | ID_PUNESOUTH | 521567 | BANER GAON | PUNE-2 | ATS | VIPIN GUPTA | SMPS | RM Faulty | 2 RM added | Closed | 2025-03-31 | 0.5 | 0.5 | 0.5 |  | 3
283 | PUN872 | IDMH108448 | NON DG | ID_PUNENORTH | 459111 | ONE NORTH-MAGARPATTA | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Cable | DCDB to RRU long distance 30 m | cable distance reduction req | Open | VIL Support Required |  | 1 |  |  | 1
284 | NAND45 | IDMH109010 | DG | ID_NANDED | 565352 | KAILASH NAGAR / KALYAN NAGAR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Backplane faulty | SMPS replaced | Closed | 2025-04-24 | 4.5 | 2.5 | 10 | 4 | 4
285 | SHML01 | IDMH109068 | DG | ID_NASHIK | 523931 | SHEMALI_NASHIK | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 2 |  | 1
286 | SANG01 | IDMH103118 | DG | ID_KOLHAPUR | 459704 | MAHALAXMI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
287 | KHMG01 | IDMH103182 | DG | ID_PUNESOUTH | 459311 | KHAMGAON BK | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Cable | DCDB to RRU long distance 45 m | cable distance reduction req | Open | VIL Support Required |  | 1 |  |  | 1
288 | KOLP11 | IDMH103183 | DG | ID_KOLHAPUR | 459755 | SHUKRAWAR PETH | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
289 | WRDH02 | INMH408320 |  | ID_NAGPUR | 458253 | SEVAGRAM | NAGPUR | NonActive | VIVEK GANJARE | SMPS | SMPS Controller faulty | PP Controller changed | Closed | 2025-01-30 | 1 |  |  |  | 1
290 | STPL01 | IDMH103327 | DG | ID_SATARA | 505479 | SHETPHALE | KOLHAPUR | SSS | VIVEK DESHPANDE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 2 | 2
291 | PAJ104 | IDMH103993 | DG | ID_GOA | 461444 | XELDEM | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-10 | 1 |  | 1.5 |  | 2
292 | KBAN01 | INMH001693 | DG | ID_KOLHAPUR | 566924 | KOLBANDRA | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
293 | NSRP04 | INMH407122 | NON DG | ID_PUNESOUTH | 451581 | NAVSAHYADRI_VF | PUNE-2 | ATS | RAHUL TUPARE | SMPS | SMPS BER | SMPS Replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
294 | NIZM01 | IDMH106433 | DG | ID_RAIGARH | 459675 | NIZAMPUR | PUNE-2 | ATS | AMAY DORUGADE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-03-16 |  | 1.5 | 0.5 | 2 | 3
295 | PUN283 | IDMH107333 | NON DG | ID_PUNENORTH | 458771 | BIRLA HOSPITAL | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Cable | DCDB to RRU Distance > 150 Mtr & Voltage drop during EB is 6 V & During BB 10 V | VIL To replace cablefrom 6-10 sqmm but not possible due to authority issue | Open | VIL Support Required | 2.5 | 4 | 4 | 5 | 4
296 | GANW01 | IDMH103779 | DG | ID_SATARA | 459428 | GANESHWADI (BAWADA) | SOLAPUR | SAI | CHANDRAKANT ANGADI | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 1 |  |  | 2
297 | CHKN09 | IDMH105153 | DG | ID_PUNENORTH | 459665 | CHAKAN MARKETYARD | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB Backup Very Low | BB replaced | Closed | 2025-04-24 | 1 | 1.5 | 0.5 | 1 | 4
298 | PUNE17 | IDMH105227 | DG | ID_PUNENORTH | 464860 | DEEP HEIGHTS | PUNE-1 | SAI | VIJAY KOLI | BB | BB Backup Very Low | BB replaced | Closed | 2025-02-08 |  | 1 |  |  | 1
299 | KWND01 | IDMH102694 | DG | ID_AKOLA | 458544 | KARWAND | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
300 | KHDE01 | IDMH104357 | DG | ID_NASHIK | 458000 | KHEDE | NASHIK | ATS | NILESH BHAVSAR | Cable | Voltage from DCDB TO RRU > 6 v | VIL to replace Cable | Open | VIL Support Required |  | 0.5 |  |  | 1
301 | SHWD01 | IDMH106017 | DG | ID_NASHIK | 464831 | SHIRWADEWANI | NASHIK | ATS | Vacant Vacant CE Nashik | RRU | RUS BTS | All infra OK & VIL to check RUS BTS | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
302 | AMVT66 | IDMH110948 | DG | ID_AMRAVATI | 523625 | ITWARA BAJAR | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS LVD & sensing card Faulty & BB Cell Faulty | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
303 | ITKR01 | IDMH111387 | DG | ID_SOLAPUR | 459052 | ITKUR | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | Smps Lvd Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
304 | AMVT28 | IDMH111508 | DG | ID_AMRAVATI | 566215 | UTTAM NAGAR NAGPUR | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
305 | NAND53 | IDMH108425 | DG | ID_NANDED | 531352 | BIG BAZAR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Backplane faulty | SMPS replaced | Closed | 2025-04-24 | 1 |  |  |  | 1
306 | PUN328 | IDMH105163 | NON DG(MSC Sharing) | ID_PUNESOUTH | 459121 | VEGA CENTRE | PUNE-2 | ATS | RAHUL TUPARE | BB | BB Backup very low | BB replaced | Reopen | 2025-03-16 |  | 1.5 | 0.5 | 1 | 3
307 | DGLR02 | IDMH108384 | DG | ID_NANDED | 565733 | DEGLUR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS BER | Replacement Pending | Open | 2025-04-30 | 0.5 |  |  | 1 | 2
308 | NSK263 | IDMH110836 | DG | ID_NASHIK | 576977 | JAI BHAWANI ROAD 2 | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
309 | SIPR06 | IDMH111582 | DG | ID_NASHIK | 507094 | SHIRPUR | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
310 | NGP297 | IDMH112182 | DG | ID_NAGPUR | 565708 | NARI INDUSTRIAL AREA | NAGPUR | SAI | LEELADHAR BHOSKAR | SMPS | SMPS Faulty | Rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
311 | LNVL33 | INMH401347 | NON DG | ID_RAIGARH | 530238 | TROISE MALL | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS Controller Faulty | SMPS replaced | Closed | 2025-01-22 | 2 |  |  |  | 1
312 | PU1155 | IDMH112359 | DG | ID_PUNENORTH | 530157 | NEAR AKSHARA INTERNATIONAL | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1.5 |  |  | 1
313 | KOL120 | IDMH112646 | DG | ID_KOLHAPUR | 566572 | GANDHINAGAR MARKET | KOLHAPUR | SSS | SANTOSH JADHAV | RRU | RRU Faulty | Support req | Open | VIL Support Required |  |  | 1 |  | 1
314 | PUN655 | IDMH105361 | DG | ID_PUNESOUTH | 459461 | NYATI SERENITY ? MOHAMADWADI (FI) | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS Backplane faulty | SMPS rectification done | Reopen | 2025-03-31 |  | 1 | 1.5 | 1 | 3
315 | BHDW01 | IDMH103504 | DG | ID_KOLHAPUR | 458916 | BHADAWAN | KOLHAPUR | SSS | RITESH RANGOLE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  | 1 | 2
316 | GKLI01 | IDMH104068 | DG | ID_SATARA | 459315 | GOKHALI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD - BLVD Faulty SR NO 23R234402N04800723 TT NO 250219CM3070811 | SMPS rectification done | Closed | 2025-04-24 |  | 0.5 |  |  | 1
317 | ISRL01 | IDMH109154 | DG | ID_AKOLA | 523900 | ISRAL | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 |  | 1.5 |  |  | 1
318 | PUN745 | IDMH105427 | NON DG | ID_PUNENORTH | 464861 | CYBAGE | PUNE-1 | SAI | VIJAY KOLI | Cable | DCDB to RRU Long distance 200m cable underrated | cable to be replace | Open | VIL Support Required |  | 0.5 |  |  | 1
319 | ANGP01 | IDMH105808 | DG | ID_SATARA | 505487 | ANGAPUR | KOLHAPUR | SSS | VINAYAK KOLEKAR | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 1 |  |  |  | 1
320 | KSBA01 | IDMH101060 | DG | ID_AMRAVATI | 507112 | MAHAGAON (KASBA) | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS Controller Faulty | SMPS rectification done | Closed | 2025-04-24 | 3.5 | 1.5 | 0.5 |  | 3
321 | MLVN01 | IDMH107116 | DG | ID_GOA | 505132 | MALVAN | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  | 0.5 | 0.5 |  | 2
322 | KOLP91 | IDMH112187 | DG | ID_KOLHAPUR | 565942 | SHIVAJI PARK | KOLHAPUR | SSS | RITESH RANGOLE | Cable | RRU Underrated cable | Need to replace cable | Open | VIL Support Required | 3 | 0.5 | 1 | 1 | 4
323 | PU2732 | INMH406010 | DG | ID_PUNESOUTH | 592630 | BlueRidge Township | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | BB | Battery Bank Theft | BB replacement required against FIR | Open | 2025-05-07 | 0.5 | 1.5 | 1.5 | 1 | 4
324 | HRCP01 | IDMH109085 | DG | ID_KOLHAPUR | 523956 | HASHURCHAMPU | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD & BLVD Strip Bern SR NO 23R1740C1004804571 TT NO 250313CM3127247 | SMPS rectification done | Closed | 2025-04-24 |  |  | 0.5 | 1 | 2
325 | GLGN01 | IDMH102120 | DG | ID_AURANGABAD | 458556 | GOLEGAON | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 1 |  |  | 1
326 | GDNJ04 | INMHVF4776 | DG | ID_KOLHAPUR | 566583 | GADHINGLAJ-III | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 1 |  |  |  | 1
327 | PAJM27 | IDMH106009 | DG | ID_GOA | 464825 | SANVORDEM | GOA | SSS | SUNIL TAMSE | SMPS | LVD faulty | SMPS replaced | Closed | 2025-04-24 | 1 |  |  |  | 1
328 | PU1057 | IDMH110076 | NON DG | ID_PUNENORTH | 459349 | TECH CENTRE YERWADA | PUNE-1 | SAI | VIJAY KOLI | SMPS | Controller Faulty Lvd Bypass | SMPS Rectification done | Reopen | 2025-03-31 |  | 1.5 |  | 1 | 2
329 | MDWD01 | IDMH102127 | DG | ID_PUNESOUTH | 459741 | MADANWADI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
330 | CFLA01 | IDMH104012 | DG | ID_PUNESOUTH | 459410 | CHAUFULLA | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
331 | BRBA01 | IDMH101691 | DG | ID_NANDED | 505322 | BARBADA | LATUR | PTPL | RAJKUMAR ALANE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 1 | 1 |  |  | 2
332 | PUN241 | IDMH106939 | DG | ID_PUNENORTH | 458781 | KUDAL WADI,CHIKALI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 | 4 | 2
333 | AUND01 | IDMH104210 | DG | ID_SATARA | 458846 | AUNDH | KOLHAPUR | SSS | VINOD SAWANT | Load Segregation | RRU at Critical | 1 RRU from critical shifted | Closed | 2025-01-30 | 0.5 |  |  |  | 1
334 | JRJI01 | IDMH112422 | DG | ID_PUNESOUTH | 459742 | JEJURI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | Smps Obsulate Model | Replacement Pending | Open | 2025-04-30 | 1 | 2 | 0.5 |  | 3
335 | CHOL01 | IDMH104473 | DG | ID_NASHIK | 458074 | CHIKHALHOL | NASHIK | ATS | SWAPNIL SALWE | Cable | SMPS LVD Faulty & Voltage from DCDB TO RRU > 2 v | ATC replaced LVD & VIL to replace Cable | Open | VIL Support Required |  | 1 | 0.5 | 3 | 3
336 | VTBR01 | IDMH105944 | DG | ID_NASHIK | 458551 | VATABARI(GHAGBARI) | NASHIK | ATS | MANOJ SINHA | SMPS | LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 2.5 | 2 | 0.5 |  | 3
337 | LOMA01 | IDMH103003 | DG | ID_AHMEDNAGAR | 505465 | LONI MAVLA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | Cable | Under Rated cable | VIL to Replace Cable | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
338 | GHUS07 | INMH002724 | DG | ID_CHANDRAPUR | 505308 | WCL GUGGUS | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
339 | PRLI04 | IDMH102369 | DG | ID_AHMEDNAGAR | 565731 | PARLI-4 | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
340 | PU1453 | IDMH100043 | NON DG | ID_PUNESOUTH | 465840 | TUKAI DARSHAN | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
341 | BRTK01 | IDMH100112 | DG | ID_AKOLA | 464905 | BARSHI TAKLI | AKOLA | SAI | Vacant CE Akola | Load Segregation | RRU at Critical | Cable change to Non critical | Closed | 2025-01-30 | 0.5 |  |  |  | 1
342 | CHND02 | IDMH100182 | DG | ID_CHANDRAPUR | 460139 | GIRNAR CHOWK | NAGPUR | SAI | GANESH DANDALWAR | RRU | RRU faulty | RRU rectification req | Open | VIL Support Required |  | 0.5 |  | 5 | 2
343 | LATR62 | INMH407513 | DG | ID_SOLAPUR | 565329 | SARTHAK NIWAS, VITTHAL SOCIETY | LATUR | PTPL | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
344 | NGPR28 | IDMH100320 | DG | ID_NAGPUR | 458324 | BALAJI-UJAY, BHARTNAGAR | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
345 | SNLI01 | IDMH100380 | DG | ID_CHANDRAPUR | 451260 | SONURLI_USO_V | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 1.5 | 3 | 2
346 | TLGN24 | IDMH108355 | DG | ID_RAIGARH | 523540 | VARALE | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS LVD Faulty | Complaint Raised to delta | Open | 2025-04-30 | 3 |  |  |  | 1
347 | FTER01 | IDMH109302 | DG | ID_NASHIK | 525937 | FATTEPUR_USO | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-02-15 | 1 |  |  |  | 1
348 | WORA01 | IDMH100428 | DG | ID_CHANDRAPUR | 460179 | WARORA | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller faulty | Plan for rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
349 | NGPR56 | IDMH100432 | DG | ID_NAGPUR | 464902 | PARDI NAKA | NAGPUR | SAI | MILIND RAMTEKE | SMPS | RM FAULTY | RM REPLACED | Closed | 2025-01-30 | 1 |  |  |  | 1
350 | NGP134 | IDMH100435 | DG | ID_NAGPUR | 505365 | PARDI | NAGPUR | SAI | MILIND RAMTEKE | SMPS | CONTROLLER FAULTY, BLVD/SPD FAULTY | Plan for rectification | Open | 2025-04-20 | 1.5 |  | 1 | 1 | 3
351 | PU2008 | IDMH100479 | DG | ID_PUNENORTH | 465699 | KEMSEVASTI WAKAD | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
352 | SDWF01 | IDMH100509 | DG | ID_CHANDRAPUR | 458133 | SHENDURWAFA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
353 | WORA04 | IDMH100592 | DG | ID_CHANDRAPUR | 460178 | KALBUT HOUSE | NAGPUR | SAI | GANESH DANDALWAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
354 | NNNJ01 | IDMH104007 | DG | ID_AHMEDNAGAR | 507081 | NAANAJ | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | RRU | RRU Faulty | RRU replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
355 | NGP153 | IDMH100644 | DG | ID_NAGPUR | 565459 | RAMESHWARI | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Obsolute model | smps replacement required | Open | 2025-05-30 | 0.5 |  |  |  | 1
356 | BHLR01 | IDMH100648 | DG | ID_CHANDRAPUR | 505241 | BHALLAR TOWNSHIP- WANI | NAGPUR | SAI | GANESH DANDALWAR | RRU | RRU faulty | RRU rectification req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
357 | MJRI01 | IDMH100650 | DG | ID_CHANDRAPUR | 460362 | MAJRI | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS Controller Faulty | Quotation received, NFA pending | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
358 | NGP196 | IDMH100700 | NON DG | ID_NAGPUR | 458380 | SHREE MOHINI COMPLEX | NAGPUR | INHOUSE | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
359 | PLGD01 | IDMH100803 | DG | ID_KOLHAPUR | 566932 | PALGAD | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 0.5 | 0.5 |  | 3
360 | PUN865 | IDMH107628 | NON DG | ID_PUNENORTH | 459269 | COMMERCE ZONE | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
361 | NERD01 | IDMH100882 | DG | ID_CHANDRAPUR | 451415 | KAYAR (NERAD) | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS Delta controller faulty Delta 4000 W | SMPS Recrification require | Open | 2025-05-15 | 2 |  | 1.5 | 4 | 3
362 | RAJN01 | IDMH106147 | DG | ID_AURANGABAD | 460299 | RANJANGAON POL | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Theft | RRU Cable damaged by unkown person | CCTV Camera installed at site | Closed | 2025-02-28 |  | 0.5 |  |  | 1
363 | MGOA08 | IDMH106291 | DG | ID_RAIGARH | 507042 | POLADPUR | PUNE-2 | ATS | AMAY DORUGADE | BB | BB Backup very low | BB replaced | Closed | 2025-03-31 | 2 |  | 0.5 |  | 2
364 | PULJ01 | IDMH103874 | DG | ID_SATARA | 458642 | PULUJ | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Back panal faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
365 | TKLG01 | IDMH101049 | DG | ID_NAGPUR | 458004 | TAKALGHAT | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS Controller faulty | SMPS Rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
366 | NGPR20 | IDMH101088 | DG | ID_NAGPUR | 458346 | C A ROAD | NAGPUR | SAI | LEELADHAR BHOSKAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 | 2 | 1 |  |  | 2
367 | RUEE01 | IDMH101839 | DG | ID_AMRAVATI | 460202 | RUI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Delta SMPS LVD card Faulty | Delta SMPS LVD card Faulty | Open | 2025-05-22 | 1 |  |  |  | 1
368 | BEED10 | IDMH101142 | DG | ID_AHMEDNAGAR | 565583 | MONDHA ROAD | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS BER | SMPS replaced | Closed | 2025-03-10 |  | 0.5 | 0.5 |  | 2
369 | BOHD01 | IDMH101216 | DG | ID_NANDED | 505329 | BODHADI BK. | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 | 0.5 |  |  | 2
370 | PU1445 | IDMH101365 | DG | ID_PUNESOUTH | 566960 | KALEPADAL ROAD | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 |  | 0.5 | 0.5 |  | 2
371 | PUN601 | IDMH103985 | DG | ID_PUNESOUTH | 507106 | WADKI | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
372 | WDAJ01 | IDMH101386 | DG | ID_NANDED | 505334 | PETH WADUJ | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Controller faulty | SMPS Controller Work Req | Open | 2025-05-22 |  | 2.5 |  |  | 1
373 | PU1461 | IDMH101466 | NON DG | ID_PUNESOUTH | 578091 | HADAPSARGAON | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-24 |  |  | 0.5 | 1 | 2
374 | HINJ14 | IDMH105857 | NON DG | ID_PUNESOUTH | 459029 | HINJEWADI CHOWK | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
375 | PAUN01 | IDMH101661 | DG | ID_NAGPUR | 458011 | PAUNI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU faulty | Support req | Open | VIL Support Required |  |  | 0.5 |  | 1
376 | KRJG01 | IDMH102323 | NON DG | ID_AMRAVATI | 458166 | KARAJGAON | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
377 | KGNI01 | IDMH102110 | DG | ID_SATARA | 505326 | KARGANI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
378 | PUN460 | IDMH102395 | NON DG | ID_PUNESOUTH | 465701 | RELN OF KATRAJ-KONDHVA ROAD | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
379 | NAND74 | IDMH110316 | DG | ID_NANDED | 576627 | BHAGYA NAGAR | LATUR | PTPL | RAJKUMAR ALANE | Load Segregation | Baseband connected Cirtcal | Plan for load separation | Open | 2025-04-20 |  | 0.5 | 1 |  | 2
380 | UMPR01 | IDMH102684 | DG | ID_AURANGABAD | 460130 | UMAPUR | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS Controller and RM slot | SMPS replaced | Closed | 2025-04-24 |  | 2 |  |  | 1
381 | DAON01 | IDMH102704 | DG | ID_SATARA | 459368 | DAHIGAON | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 2.5 |  |  | 2
382 | PAJ504 | IDMH112257 | NON DG | ID_GOA | 465712 | FATORDA | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Backpanel Faulty SR NO 20161271IG0316 | Plan for rectification | Open | 2025-04-30 |  |  | 1.5 | 1 | 2
383 | NVRJ01 | IDMH102739 | DG | ID_AHMEDNAGAR | 459988 | NAVGAN RAJURI | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS BER | Plan for SMPS Replacement | Open | 2025-05-30 |  | 1.5 |  |  | 1
384 | KOKE01 | IDMH102763 | DG | ID_KOLHAPUR | 459588 | KOKALE | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
385 | SRGD06 | INMH405759 | DG | ID_AHMEDNAGAR | 566817 | OPEN PLOT SHRIGONDA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-12 | 0.5 | 1 | 0.5 |  | 3
386 | ATPD02 | IDMH102833 | DG | ID_SATARA | 505500 | ATPADI | KOLHAPUR | SSS | VIVEK DESHPANDE | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
387 | PLSH01 | IDMH102896 | DG | ID_SATARA | 459430 | PALSHI | KOLHAPUR | SSS | VINOD SAWANT | SMPS | SMPS Controller _LVD & BLVD Faulty TT NO 250308CM3119066 | Plan for rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
388 | PLMR01 | IDMH102916 | DG | ID_KOLHAPUR | 459548 | PETH ISLAMPUR | KOLHAPUR | SSS | VINOD SAWANT | SMPS | SMPS Controller Faulty DC Fan Faulty SR NO 23R204425A04803877 TT NO 250113CM2982768 | SMPS Rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
389 | RAJR01 | IDMH100015 | DG | ID_CHANDRAPUR | 567147 | RAJURA | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 | 0.5 |  |  | 2
390 | NARA01 | IDMH100027 | DG | ID_NAGPUR | 457958 | NARA | NAGPUR | SAI | VIVEK GANJARE | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
391 | STKH04 | IDMH103126 | DG | ID_KOLHAPUR | 458655 | SAJANI | KOLHAPUR | SSS | SANTOSH JADHAV | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
392 | SLLI01 | IDMH103188 | DG | ID_KOLHAPUR | 461290 | SHINOLI KH. | KOLHAPUR | SSS | RITESH RANGOLE | BB | Low battery backup | Need to replace BB | Open | 2025-05-30 | 1.5 |  |  |  | 1
393 | MJWD01 | IDMH103300 | DG | ID_NASHIK | 458070 | MUNJWAD | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS Backplane faulty | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
394 | NGPR71 | IDMH100087 | DG | ID_NAGPUR | 565399 | KETAN HYUNDAI | NAGPUR | SAI | KAILASH POKALE | RRU | 2-RRU Cable cascaded & Voltage drop 3 V | VIL to rectify | Open | VIL Support Required |  |  | 0.5 |  | 1
395 | ABLE01 | IDMH103416 | DG | ID_PUNESOUTH | 459518 | AMBALE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 1 | 1.5 | 1 | 1 | 4
396 | DUGN01 | IDMH103447 | DG | ID_NASHIK | 458435 | DUGAON | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS LVD faulty | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
397 | ABDS01 | IDMH103611 | DG | ID_KOLHAPUR | 465859 | AMBADAS | KOLHAPUR | SSS | VIVEK GOSAVI | RRU | RRU Issue | VIL Support require | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
398 | PNAB03 | IDMH103634 | DG | ID_PUNENORTH | 459660 | KAREGAON | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  |  | 1 | 1 | 2
399 | VKML01 | IDMH103649 | DG | ID_SATARA | 458904 | VARKUTE MALAVADI | KOLHAPUR | SSS | VINAYAK KOLEKAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-10 |  | 1.5 |  |  | 1
400 | KDRJ01 | IDMH103668 | DG | ID_KOLHAPUR | 459650 | KHANDERAJURI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
401 | PAJ558 | IDMH100151 | NON DG | ID_GOA | 465785 | CLUB MAHINDRA RESORT, VARCA | GOA | SSS | SUNIL TAMSE | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
402 | LSRN01 | IDMH103777 | DG | ID_PUNESOUTH | 459275 | LASURNE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
403 | YAVT01 | IDMH100159 | DG | ID_AMRAVATI | 458402 | HOTEL RAMAYAN | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Smps Lvd Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
404 | GNKD02 | IDMH100162 | DG | ID_NANDED | 505096 | GANGAKHED RPTR(GBT) | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | BB | BB Backup very low | BB replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
405 | HRDL01 | IDMH100178 | DG | ID_CHANDRAPUR | 458077 | HARDOLI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | Smps Controller Faulty | SMPS replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
406 | KLDN01 | IDMH103906 | DG | ID_SATARA | 459006 | KALEDHON | KOLHAPUR | SSS | VINOD SAWANT | SMPS | LVD bypassed | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
407 | SANG24 | IDMH103959 | DG | ID_KOLHAPUR | 566051 | BUS STAND_SANGLI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-03-31 | 0.5 |  | 0.5 |  | 2
408 | KRVE01 | IDMH104030 | DG | ID_SATARA | 459380 | KARVE | KOLHAPUR | SSS | VINOD SAWANT | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
409 | HNGA01 | IDMH104046 | DG | ID_AHMEDNAGAR | 505464 | HANGA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | LVD/BLVD faulty | Plan for rectification | Open | 2025-04-20 |  | 0.5 | 0.5 |  | 2
410 | PRKS01 | IDMH104098 | DG | ID_NASHIK | 458008 | PRAKASHA | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
411 | MRTI01 | IDMH104166 | DG | ID_PUNESOUTH | 458695 | MURTI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | Controller Faulty | Plan for rectification | Open | 2025-05-15 | 0.5 | 1 |  |  | 2
412 | KOLP31 | IDMH104206 | DG | ID_KOLHAPUR | 565901 | KALAMBA, V R ESTATE | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
413 | PAJM44 | IDMH104225 | DG | ID_GOA | 566228 | BAMBOLIN | GOA | SSS | SURAJ PATIL | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-02-05 |  | 0.5 |  |  | 1
414 | PAAL01 | IDMH104252 | DG | ID_SATARA | 458951 | PAL | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD Faulty | LVD Bypass | Open | 2025-04-20 | 1.5 |  | 0.5 |  | 2
415 | KRLW01 | IDMH104365 | DG | ID_KOLHAPUR | 459491 | KIRLOSKARWADI | KOLHAPUR | SSS | VIVEK DESHPANDE | BB | BB 5 cell faulty/Backup 15min | Need to replace faulty cell/Under waranty | Open | 2025-05-15 | 4.5 | 2.5 |  |  | 2
416 | NMSD01 | IDMH104399 | DG | ID_SATARA | 459000 | NIMSOD | KOLHAPUR | SSS | VINOD SAWANT | SMPS | LVD bypassed | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
417 | ALTE01 | IDMH104410 | DG | ID_KOLHAPUR | 459802 | AALTE | KOLHAPUR | SSS | SANTOSH JADHAV | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
418 | NOOL01 | IDMH104417 | DG | ID_KOLHAPUR | 505332 | KASBA NOOL | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
419 | YESG01 | IDMH104429 | DG | ID_NASHIK | 458460 | YESGAON BK. | NASHIK | ATS | SWAPNIL SALWE | BB | Battery backup very low | BB replaced | Closed | 2025-04-24 | 0.5 | 1 |  |  | 2
420 | SVBK01 | IDMH104468 | DG | ID_KOLHAPUR | 458962 | SAWARDE BK. | KOLHAPUR | SSS | RITESH RANGOLE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
421 | TLDH01 | IDMH104477 | DG | ID_PUNENORTH | 458861 | TALEGAON DHAMDHERE | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 1.5 | 3 |  |  | 2
422 | NIBT01 | IDMH104490 | DG | ID_PUNESOUTH | 458897 | NIMBUT | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  | 0.5 |  | 2
423 | CHRL01 | IDMH100331 | DG | ID_AMRAVATI | 458110 | CHANDUR RAILWAY | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
424 | NGAL10 | IDMH100342 | DG | ID_AKOLA | 458252 | BORGAON MANJU | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
425 | PAJ230 | IDMH104516 | NON DG | ID_GOA | 565878 | OLD ANCHOR RESORT | GOA | SSS | SUNIL TAMSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
426 | JKWD01 | IDMH104522 | DG | ID_SATARA | 566298 | YEWATESHWAR | KOLHAPUR | SSS | VINAYAK KOLEKAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-10 |  | 0.5 |  |  | 1
427 | PUN329 | IDMH104524 | DG | ID_PUNENORTH | 464798 | ZENSAR KHARADI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 1 |  | 1 | 3
428 | BVCH01 | IDMH104543 | DG | ID_KOLHAPUR | 507084 | BAVCHI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
429 | PTKD01 | IDMH104544 | DG | ID_KOLHAPUR | 458669 | PATTAN KODOLI | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Reopen | 2025-01-30 | 1.5 |  |  | 2 | 2
430 | SHYE01 | IDMH104553 | DG | ID_KOLHAPUR | 459804 | SHIYE | KOLHAPUR | SSS | SANTOSH JADHAV | VIL Planned Activity | L900work done | NA | Closed | 2025-03-31 | 0.5 |  | 0.5 |  | 2
431 | PUNE02 | IDMH104560 | DG | ID_PUNESOUTH | 459228 | HERMES NOOK | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  | 2 | 2
432 | PUN461 | IDMH104591 | DG | ID_PUNESOUTH | 459464 | WADKI | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
433 | PUN110 | IDMH104607 | NON DG | ID_PUNENORTH | 459229 | TAJ BLUE DIAMOND,PUNE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | Smps Controller Faulty | Plan for rectification | Open | 2025-05-07 | 2 | 1 | 0.5 | 1 | 4
434 | MIRJ03 | IDMH104625 | DG | ID_KOLHAPUR | 459710 | MIRAJ MAIN MARKET | KOLHAPUR | SSS | VIVEK DESHPANDE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
435 | TSGN01 | IDMH104638 | DG | ID_KOLHAPUR | 459547 | SYYED PLOT | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
436 | DMOD01 | IDMH104650 | DG | ID_KOLHAPUR | 458854 | DHAMOD | KOLHAPUR | SSS | RITESH RANGOLE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
437 | PUNE89 | IDMH104657 | DG | ID_PUNESOUTH | 459400 | NYATI ESTATE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  | 2 | 3
438 | PUN183 | IDMH104716 | DG | ID_PUNENORTH | 464881 | WADGAON SHERI | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
439 | DUND01 | IDMH104725 | DG | ID_PUNESOUTH | 459452 | DAUND | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 0.5 | 2 | 2 | 1 | 4
440 | PAJ271 | IDMH104730 | NON DG | ID_GOA | 461451 | INTER CONTINENTAL | GOA | SSS | SUNIL TAMSE | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-04-24 | 1 | 0.5 | 0.5 |  | 3
441 | PCHE01 | IDMH104734 | DG | ID_PUNESOUTH | 458823 | PARINCHE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 |  |  | 0.5 |  | 1
442 | GRGN01 | IDMH100502 | DG | ID_NANDED | 460203 | GOREGAON | AKOLA | SAI | ALI SHAH | SMPS | SMPS BER | Replacement Pending | Open | 2025-05-30 | 0.5 |  |  |  | 1
443 | MIRJ09 | IDMH104763 | DG | ID_KOLHAPUR | 459713 | MIRAJ MIDC II | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
444 | VHRN01 | IDMH100519 | DG | ID_CHANDRAPUR | 451439 | VIHIRGAON | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 0.5 |  | 1
445 | PNST05 | IDMH104796 | DG | ID_SATARA | 459577 | AMRITHWADI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
446 | NRMR01 | IDMH104808 | DG | ID_NASHIK | 460063 | NANDUR MADHYAMESHWAR | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  |  | 1
447 | PAJM81 | IDMH104819 | DG | ID_GOA | 461401 | ZUARINAGAR | GOA | SSS | SUNIL TAMSE | SMPS | SMPS controller faulty | New SMPS Received, I&C Pendingg | Open | 2025-04-30 | 0.5 |  |  |  | 1
448 | TKBH01 | IDMH104825 | DG | ID_PUNENORTH | 458865 | TAKLI BHIMA | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 |  | 1 | 1 | 3
449 | RTBK01 | IDMH104827 | DG | ID_SATARA | 459482 | RETHRE BUDRUK | KOLHAPUR | SSS | VINOD SAWANT | BB | zero backup site | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
450 | KHTV01 | IDMH104840 | DG | ID_SATARA | 458643 | KHATAV | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
451 | NRYN02 | IDMH104956 | DG | ID_RAIGARH | 460358 | WARULWADI | PUNE-1 | ATS | SWAPNIL KARAD | RRU | BSS RRU installation Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
452 | PAJ186 | IDMH104977 | NON DG | ID_GOA | 461391 | PELIEM | GOA | SSS | SUNIL TAMSE | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
453 | PAJM38 | IDMH104992 | DG | ID_GOA | 464824 | COLA | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Display and LVD faulty | Rectifcation done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
454 | PUN753 | IDMH105002 | NON DG | ID_PUNENORTH | 464862 | EON | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
455 | NGPR83 | IDMH100588 | DG | ID_NAGPUR | 458365 | IMAMWADA | NAGPUR | SAI | MILIND RAMTEKE | SMPS | Smps Lvd Faulty | Rectification Done | Closed | 2025-03-07 | 0.5 |  | 0.5 |  | 2
456 | PNAB02 | IDMH105023 | DG | ID_PUNENORTH | 458681 | SHIKRAPUR | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
457 | PMPD01 | IDMH105036 | DG | ID_SATARA | 459427 | PIMPODE BUDRUK | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
458 | PUN266 | IDMH105059 | NON DG | ID_PUNESOUTH | 459162 | SONY WORLD | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
459 | GNWR01 | IDMH105097 | DG | ID_SATARA | 459319 | GUNAWARE | KOLHAPUR | SSS | VINAYAK KOLEKAR | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 2 | 4.5 | 2.5 |  | 3
460 | DBHL01 | IDMH105127 | DG | ID_KOLHAPUR | 458905 | RANAVI-DABHOL | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LLVD/BLVD Faulty | DG replacement/ SMPS LLVD/BLVD replacement Pending | Open | 2025-05-15 | 0.5 | 1 |  | 2 | 3
461 | SINR02 | IDMH105132 | DG | ID_NASHIK | 460335 | SINNERGAON | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
462 | BLAJ01 | IDMH100640 | DG | ID_PUNESOUTH | 505200 | PUNE SATARA ROAD MINI BALAJI | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-02-28 |  | 2.5 |  |  | 1
463 | ANVL01 | IDMH105133 | DG | ID_KOLHAPUR | 458849 | MOUJE ANJANVEL | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 1 |  |  |  | 1
464 | SATR08 | IDMH105281 | DG | ID_SATARA | 458633 | KHED | KOLHAPUR | SSS | VINAYAK KOLEKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
465 | PUNE01 | IDMH105299 | DG | ID_PUNESOUTH | 459243 | ATUR CHAMBERS | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
466 | NBLK01 | IDMH105388 | DG | ID_AHMEDNAGAR | 507064 | NIMBLAK | AHMEDNAGAR | PTPL | NILESH NAGDEVE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
467 | PUSH01 | IDMH105407 | DG | ID_KOLHAPUR | 459015 | PUSHPANAGAR | KOLHAPUR | SSS | RITESH RANGOLE | BB | BB 6 cell faulty/Backup 15min | Cell replaced | Closed | 2025-04-24 | 2.5 | 0.5 | 1 |  | 3
468 | PUN405 | IDMH105440 | DG | ID_PUNESOUTH | 459118 | HADAPSAR MIDC | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
469 | HTVL01 | IDMH105550 | DG | ID_KOLHAPUR | 458719 | HATIVALE | KOLHAPUR | SSS | VIVEK GOSAVI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
470 | PUNE82 | IDMH105554 | DG | ID_PUNESOUTH | 459104 | RAVI PARK (RELOCATION) | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
471 | PUN392 | IDMH105571 | DG | ID_PUNESOUTH | 459401 | MOHAMMADWADI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
472 | TKVD01 | IDMH105573 | DG | ID_KOLHAPUR | 505265 | TAKAVADE | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 |  | 1.5 |  | 2
473 | PAJ353 | IDMH107137 | DG | ID_GOA | 523288 | ASSNORA 2-MLG | GOA | SSS | SURAJ PATIL | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-04-24 |  | 0.5 | 0.5 |  | 2
474 | PRLE01 | IDMH105604 | DG | ID_KOLHAPUR | 507068 | PORLE T THANE | KOLHAPUR | SSS | SANTOSH JADHAV | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 2 |  |  | 2
475 | SRIL01 | IDMH105643 | DG | ID_KOLHAPUR | 458651 | SHIROL | KOLHAPUR | SSS | SANTOSH JADHAV | VIL Planned Activity | L900work done | NA | Closed | 2025-03-31 |  | 0.5 |  |  | 1
476 | MLGN02 | IDMH105646 | DG | ID_NASHIK | 458054 | PACH KANDIL | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
477 | PUN181 | IDMH105650 | DG | ID_PUNENORTH | 458787 | PIMPRI CHOWK | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
478 | KDHI01 | IDMH100802 | DG | ID_CHANDRAPUR | 451354 | KADHOLI_V_USO | NAGPUR | SAI | BEERENDRA SINGH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
479 | WADK01 | IDMH100804 | DG | ID_CHANDRAPUR | 451399 | CHAKHINTALDHABAWADKULI | NAGPUR | SAI | GANESH DANDALWAR | SMPS | Controller Faulty, Dcif Card Faulty , Cabinet Fan Faulty | Plan for rectification | Open | 2025-05-22 |  |  | 1 |  | 1
480 | SATR06 | IDMH105684 | DG | ID_SATARA | 459792 | SATARA BUS STAND | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
481 | AKLA26 | IDMH100841 | DG | ID_AKOLA | 458291 | BHIM NAGAR | AKOLA | SAI | Vacant CE Akola | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
482 | PUN154 | IDMH105719 | DG | ID_PUNESOUTH | 459211 | GANGA DHAM | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
483 | KSMB01 | IDMH105727 | DG | ID_NASHIK | 457972 | KUSUMBA | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 6 | 1
484 | PUN429 | IDMH105738 | DG | ID_PUNENORTH | 458812 | D Y PATIL COLLEGE | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | SMPS BER | SMPS replaced | Closed | 2025-04-24 | 0.5 |  |  |  | 1
485 | PU2786 | IDMH100879 |  | ID_PUNENORTH | 465836 | CHEST HOSPITAL-AUNDH | PUNE-2 | ATS | VIPIN GUPTA | BB | Low Battery Backup | BB upgradation done | Closed | 2025-04-09 | 1 |  |  | 2 | 2
486 | TBHR01 | IDMH105826 | DG | ID_NASHIK | 460188 | TRIMBAKESHWAR | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS controller faulty | SMPS replacement req | Open | 2025-05-07 | 2.5 | 0.5 | 0.5 |  | 3
487 | PUNE50 | IDMH105864 | DG | ID_PUNENORTH | 459136 | ATLATIES, KALYANI NAGAR | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
488 | LANJ01 | IDMH105898 | DG | ID_KOLHAPUR | 459715 | LANJA | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Reopen | 2025-02-28 | 0.5 | 1.5 |  | 1 | 3
489 | NZPT01 | IDMH111917 | DG | ID_SATARA | 459322 | NAZARE PHATA | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
490 | RSOD01 | IDMH100925 | DG | ID_AMRAVATI | 460114 | RISOD | AKOLA | SAI | ALI SHAH | SMPS | LVD and BLVD and controller faulty, Backplane faulty, SPD faulty | SMPS Rectification require | Open | 2025-04-20 |  | 0.5 | 0.5 | 3 | 3
491 | BLSH01 | IDMH106022 | DG | ID_KOLHAPUR | 459602 | BILASHI | KOLHAPUR | SSS | VINOD SAWANT | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
492 | PUN592 | IDMH106081 | DG | ID_PUNENORTH | 505171 | KALEWADI CHOWK | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
493 | KRDN01 | IDMH106102 | DG | ID_KOLHAPUR | 459485 | KURDHUNDA | KOLHAPUR | SSS | VIVEK GOSAVI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
494 | PUNE63 | IDMH106259 | DG | ID_PUNESOUTH | 459456 | PHURSUNGI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
495 | DPWD01 | IDMH100979 | DG | ID_NAGPUR | 458220 | DHAPEWADA BK | NAGPUR | SAI | KAILASH POKALE | Cable | Cable voltage>2.5V long distance SMPS to BTS | VIL to rectify | Open | VIL Support Required |  | 0.5 |  |  | 1
496 | GHGR01 | IDMH106359 | DG | ID_KOLHAPUR | 566922 | GUHAGHAR | KOLHAPUR | SSS | VIVEK GOSAVI | Cable | DCDB-RRH CABLE DISTANCE 85 MTR | Plan for Cable replacement | Open | VIL Support Required | 1 |  |  |  | 1
497 | NAGJ01 | IDMH106411 | DG | ID_KOLHAPUR | 459438 | NAGAJ | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 1 |  |  |  | 1
498 | SWNT02 | IDMH106448 | DG | ID_GOA | 461323 | SAWANTHWADI RAILWAY | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS Controller faulty , TT NO 230908CM1860432 TT NO 250130CM3015867 | SMPS rectification done | Closed | 2025-04-24 | 2 |  | 0.5 |  | 2
499 | CHIP05 | IDMH106493 | DG | ID_KOLHAPUR | 458909 | CHIPLUN MARKET | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
500 | BDRI01 | IDMH106582 | DG | ID_KOLHAPUR | 464838 | BIDRI | KOLHAPUR | SSS | RITESH RANGOLE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 2.5 | 0.5 |  |  | 2
501 | PUN594 | IDMH106691 | DG | ID_PUNENORTH | 505541 | WAKAD4 | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
502 | SPWD01 | IDMH106775 | DG | ID_RAIGARH | 464835 | SUPEWADI | PUNE-1 | ATS | SWAPNIL KARAD | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
503 | CHIP02 | IDMH106795 | NON DG | ID_KOLHAPUR | 458913 | KHERDI | KOLHAPUR | SSS | VIVEK GOSAVI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
504 | NASK69 | IDMH106834 | DG | ID_NASHIK | 459909 | ANANDVALLI | NASHIK | ATS | MANOJ SINHA | Load Segregation | RRU critical | RRU critical to Non critical | Closed | 2025-03-31 | 1.5 |  |  |  | 1
505 | BOHS01 | IDMH106863 | DG | ID_SATARA | 522194 | BHOSE | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS Faulty | SMPS rectification done | Closed | 2025-04-24 | 1 | 0.5 |  |  | 2
506 | PRLI08 | IDMH106879 | DG | ID_AHMEDNAGAR | 532397 | AMBEJOGAI ROAD | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
507 | LNVL14 | IDMH107368 | DG | ID_RAIGARH | 522297 | TIMBER VALLEY HOTEL GREEN LAND_A | PUNE-3 | ATS | PRATIK HULAVALE | Cable | SMPS to RRU VLTG Drop >3v | cable to replace | Open | VIL Support Required |  | 1 |  |  | 1
508 | PALE01 | IDMH101081 | DG | ID_AHMEDNAGAR | 460020 | PALI | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
509 | LNVL35 | INMH408562 | NON DG | ID_RAIGARH | 451502 | CINEBLISS_VF | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS BER | SMPS replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
510 | NMGN01 | IDMH107637 | DG | ID_PUNESOUTH | 458950 | NIMGAON KETKI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 1.5 |  |  |  | 1
511 | HINJ02 | IDMH107724 | DG | ID_PUNESOUTH | 459026 | TATA JOHNSON_HINJ02 | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
512 | NASK43 | IDMH107892 | NON DG | ID_NASHIK | 459932 | CHANDAK CIRCLE | NASHIK | ATS | MANOJ SINHA | SMPS | Voltage Drop 2 Volt ,LVD Bypass | SMPS Rectification Require | Open | 2025-04-30 |  | 0.5 |  |  | 1
513 | PU1027 | IDMH107941 | DG | ID_PUNESOUTH | 523852 | SRPF, HADAPSAR | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS Back panal faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
514 | HINJ55 | IDMH107966 | NON DG | ID_PUNESOUTH | 458981 | INFOSYS SDB 10 HINJEWADI PH-II. | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 | 2 | 2
515 | PAJ356 | IDMH108121 | DG | ID_GOA | 522310 | DHARGAL | GOA | SSS | SURAJ PATIL | SMPS | SMPS RM Faulty | RM replaced | Closed | 2025-02-11 |  | 0.5 |  |  | 1
516 | BOHL01 | IDMH111936 | DG | ID_SATARA | 458710 | BOHALI | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
517 | AMSH01 | IDMH108172 | DG | ID_KOLHAPUR | 523879 | AMASHI | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
518 | GVRI01 | IDMH101130 | DG | ID_AURANGABAD | 565578 | GEORAI, BEED | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
519 | RUEI01 | IDMH108527 | DG | ID_SATARA | 523904 | RUI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
520 | CHND30 | IDMH108558 | DG | ID_CHANDRAPUR | 567125 | NAGINA BAG | NAGPUR | SAI | GANESH DANDALWAR | RRU | RRU faulty | RRU rectification req | Open | VIL Support Required |  |  | 0.5 |  | 1
521 | ISAD01 | IDMH101137 | DG | ID_NANDED | 460021 | ISAD | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | SMPS | SMPS Backplane faulty | SMPS rectification done | Reopen | 2025-03-31 | 0.5 |  | 0.5 | 1 | 3
522 | MIRJ17 | IDMH108661 | DG | ID_KOLHAPUR | 507126 | MANIK NAGAR COLONY | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
523 | MLGN22 | IDMH108825 | DG | ID_NASHIK | 565993 | AZAD COMPLEX | NASHIK | ATS | SWAPNIL SALWE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 1.5 | 0.5 |  |  | 2
524 | PU1267 | IDMH108904 | NON DG | ID_PUNENORTH | 527345 | AKURDI_NEW | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
525 | KAKV04 | IDMH108945 | DG | ID_GOA | 567021 | KANKAVALI-3 GOA | GOA | SSS | KISHOR SHIRSATH | Cable | DCDB to RRU cable Voltage drop > 4 V | Cable Replacement Require | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
526 | ANGR44 | IDMH109036 | DG | ID_AHMEDNAGAR | 532395 | DMR_AHMEDNAGAR | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS Faulty | SMPS Replaced | Closed | 2025-01-03 | 0.5 |  |  |  | 1
527 | KURK01 | IDMH109086 | DG | ID_KOLHAPUR | 523949 | KURUKALI | KOLHAPUR | SSS | RITESH RANGOLE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
528 | KOLP93 | IDMH109127 | NON DG | ID_KOLHAPUR | 465295 | SAYAJI HOTEL | KOLHAPUR | SSS | RITESH RANGOLE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
529 | SROL02 | IDMH101190 | DG | ID_KOLHAPUR | 566353 | NH-4,SHIROLI | KOLHAPUR | SSS | SANTOSH JADHAV | BB | SMPS Calliberation issue & Backup < 15 min | SMPS Callibertion done & New BB Required | Open | 2025-04-30 |  | 0.5 |  |  | 1
530 | GAKD01 | IDMH109420 | DG | ID_NASHIK | 523985 | GARKHEDE_NASHIK | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS LVD Open Due to Lighting,Alaram & Controller Faulty | SMPS Rectification Require | Open | 2025-04-30 | 0.5 |  |  |  | 1
531 | WANI08 | IDMH109460 | DG | ID_CHANDRAPUR | 500185 | YEWATMAL- WANI 3 | NAGPUR | SAI | GANESH DANDALWAR | RRU | RRU faulty | RRU rectification req | Open | VIL Support Required |  |  | 1 |  | 1
532 | LDKD01 | IDMH101201 | DG | ID_AMRAVATI | 464936 | LADKHED | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 1 |  |  | 2
533 | RNGH01 | IDMH109553 | DG | ID_CHANDRAPUR | 523958 | RONGHA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
534 | CHKN46 | IDMH109564 | DG | ID_PUNENORTH | 525685 | MAHINDRA VEHICLES 2 | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 1 |  |  | 2
535 | DULE35 | IDMH109703 | NON DG | ID_NASHIK | 526261 | SSVPS COE_NEW. | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
536 | KWAD01 | IDMH101237 | DG | ID_AMRAVATI | 459333 | KENWAD | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
537 | PUN347 | IDMH109839 | DG | ID_PUNENORTH | 459108 | TINGRENAGAR 2_PUN347 | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 1 | 2
538 | NSK215 | IDMH110007 | DG | ID_NASHIK | 567037 | SIEMENS_NASIK | NASHIK | ATS | SUBHASH SHINDE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
539 | NGP385 | IDMH110524 | DG | ID_NAGPUR | 565486 | GURUKRIPA APPT | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
540 | MGPR01 | IDMH101258 | DG | ID_AMRAVATI | 458429 | MANGLUR PIR | AKOLA | SAI | ALI SHAH | SMPS | Smps Controller And Lvd Faulty | Rectification Pending | Open | 2025-05-15 |  | 1 | 1 | 1 | 3
541 | PAJ440 | IDMH110640 | DG | ID_GOA | 567052 | ANJUNA BEACH | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
542 | SANG41 | IDMH110706 | DG | ID_KOLHAPUR | 528536 | ANKALI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
543 | PAJM16 | IDMH105632 | DG | ID_GOA | 461395 | AGACAIM | GOA | SSS | SURAJ PATIL | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-01-04 | 0.5 |  |  |  | 1
544 | SMBT01 | IDMH110825 | NON DG | ID_NASHIK | 465433 | SMBT COLLEGE | NASHIK | ATS | SUBHASH SHINDE | Cable | RRU cable damage | cable replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
545 | WRDH04 | IDMH101293 | DG | ID_NAGPUR | 458271 | SAVANGI MEDICAL COLLEGE | NAGPUR | SAI | VIVEK GANJARE | SMPS | DCDB MCB Faulty | MCB replaced | Closed | 2025-03-31 |  |  | 2 |  | 1
546 | NSK244 | IDMH110951 | DG | ID_NASHIK | 571574 | SALUNKHE NAGAR | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS replacement | Open | 2025-04-30 | 2.5 |  |  |  | 1
547 | CHKN74 | IDMH111189 | DG | ID_PUNENORTH | 465657 | KHALUMBRE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 | 1 |  | 2
548 | PTHN01 | IDMH111254 | DG | ID_CHANDRAPUR | 451331 | PATAN | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
549 | GTAJ01 | IDMH111304 | DG | ID_CHANDRAPUR | 507070 | GUJARAT AMBUJA | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-28 |  | 1.5 |  |  | 1
550 | BGHN01 | IDMH111374 | DG | ID_NAGPUR | 458274 | BHANEGAON | NAGPUR | SAI | LEELADHAR BHOSKAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
551 | WRDH10 | IDMH111410 | DG | ID_NAGPUR | 458251 | SINDI TURF HINDNAGAR | NAGPUR | SAI | VIVEK GANJARE | SMPS | controller faulty Outdated Delta2700 PP | New SMPS Req | Open | 2025-04-30 |  | 1 |  |  | 1
552 | DHVL01 | IDMH111608 | DG | ID_NASHIK | 458142 | DAHIWEL | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 0.5 |  |  | 2
553 | SANG20 | IDMH111672 | DG | ID_KOLHAPUR | 566046 | SANGALWADI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
554 | SNSR01 | IDMH111691 | DG | ID_PUNESOUTH | 458945 | SANSAR | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
555 | CHGD02 | IDMH111713 | DG | ID_KOLHAPUR | 461287 | HALKARNI | KOLHAPUR | SSS | RITESH RANGOLE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
556 | GUMT01 | IDMH101364 | DG | ID_NAGPUR | 465826 | GAUMTHALA | NAGPUR | SAI | MILIND RAMTEKE | SMPS | Smps Controller Faulty | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
557 | PUN883 | IDMH111816 | DG | ID_PUNENORTH | 522489 | GOLDEN CASCADE - WAKAD ROAD_A | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
558 | NASK67 | IDMH111862 | NON DG | ID_NASHIK | 459924 | TARWALA NAGAR | NASHIK | ATS | MANOJ SINHA | BB | BB cell faulty | BB cell replaced | Closed | 2025-02-15 |  | 0.5 |  |  | 1
559 | PBNI09 | IDMH101387 | DG | ID_NANDED | 460168 | OLD BUS STAND | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Cable | DCDB to RRU cable Voltage drop > 4 V | Cable Replacement Require | Open | VIL Support Required | 2 |  |  |  | 1
560 | NASK79 | IDMH111879 | NON DG | ID_NASHIK | 460236 | VILHOLI | NASHIK | ATS | SUBHASH SHINDE | Cable | SMPS To RRU 90 Mtr,Distance very Long ,Voltage Drop 2.25 Volt ,DCDB to RRU 6 SQ MM Cable Used,Site In Manual Mode,Old SMPS LVD Bypass | AMF & SMPS replaced - 12-Sept & VIL to replace cable | Open | VIL Support Required | 1.5 |  | 0.5 |  | 2
561 | BHSP01 | IDMH111910 | DG | ID_KOLHAPUR | 458836 | BHARTI SHIPYARD | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
562 | KOLP71 | IDMH112023 | DG | ID_KOLHAPUR | 464805 | CIRCUIT HOUSE_COW | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
563 | CHND36 | IDMH112221 | DG | ID_CHANDRAPUR | 567136 | DEVAI GOVINDPUR | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS Controller Faulty | SMPS rectification done | Reopen | 2025-03-31 |  |  | 0.5 | 6 | 2
564 | ICKJ27 | IDMH112315 | DG | ID_KOLHAPUR | 566867 | KRISHNA NAGAR, KOLHAPUR | KOLHAPUR | SSS | SANTOSH JADHAV | VIL Planned Activity | L900work done | NA | Closed | 2025-03-31 |  | 0.5 |  |  | 1
565 | AKLA73 | IDMH112557 | DG | ID_AKOLA | 529522 | SINDHI COLONY 2_AKOLA | AKOLA | SAI | Vacant CE Akola | Load Segregation | 1 RRU Running at Critical | LVD Setting done. 45 and 42 ,1 RRU Running at Critical, Require connection at Non critical | Open | 2025-04-20 |  | 0.5 |  |  | 1
566 | NSK363 | INMH000503 | NON DG | ID_NASHIK | 576980 | ANANDWALIGAON | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
567 | PDKV03 | INMH002813 | DG | ID_CHANDRAPUR | 565955 | PANDHAKAVDA | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-20 | 1 | 0.5 |  |  | 2
568 | AKLA82 | INMH003239 | DG | ID_AKOLA | 505158 | SANT TUKARAM HOSPITAL | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
569 | YOLA06 | INMH006140 | DG | ID_NASHIK | 565977 | YEOLA | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS LVD Faulty | SMPS Rectification Require | Open | 2025-04-20 | 0.5 | 1 |  |  | 2
570 | ESHV01 | INMH006524 | DG | ID_SATARA | 459355 | EKSHIV | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
571 | PU1667 | INMH403282 | DG | ID_PUNENORTH | 576356 | LOGISTICS,WAGHOLI | PUNE-1 | ATS | HARSHAL MAHAJAN | SMPS | SMPS Controller Faulty | Controller Changed & Setting done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
572 | KADE01 | INMH403879 | DG | ID_SATARA | 465903 | Relocation of Kadegaon (KADE01) | KOLHAPUR | SSS | VINOD SAWANT | RRU | RRU Issue | VIL Support require | Open | VIL Support Required | 6.5 | 1.5 |  |  | 2
573 | ANGR10 | IDMH106474 | DG | ID_AHMEDNAGAR | 460353 | TARAKPUR | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-03-10 |  | 0.5 |  |  | 1
574 | MIRJ34 | INMH405435 | NON DG | ID_KOLHAPUR | 587370 | Gulabrao Patil College of Pharmacy | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
575 | NGAL07 | IDMH101540 | DG | ID_AMRAVATI | 458082 | TIVSA | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
576 | KOL170 | INMH405549 | NON DG | ID_KOLHAPUR | 576779 | CRUSHER CHOWK | KOLHAPUR | SSS | RITESH RANGOLE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
577 | SINR24 | INMH405774 | NON DG | ID_NASHIK | 589127 | Airtel_Shivaji Nagar | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
578 | KHAM21 | INMH405782 | NON DG | ID_AKOLA | 590844 | Sutala Khamgaon | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-20 |  | 1.5 | 2 | 2 | 3
579 | TPPA01 | IDMH101438 | DG | ID_NANDED | 459837 | TUPPA | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS Obsolute model | Plan for SMPS replacement | Open | 2025-05-07 | 1 | 4.5 | 1 | 2 | 4
580 | BIJU01 | IDMH101615 | DG | ID_NANDED | 458678 | BIJUR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS BER | SMPS Replaced | Closed | 2025-02-18 |  | 0.5 |  |  | 1
581 | DAHI01 | IDMH101616 | DG | ID_AKOLA | 464903 | DAHIHANDA | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
582 | KOLP99 | INMHVF2522 | NON DG | ID_KOLHAPUR | 451483 | BAPATCAMP_VF | KOLHAPUR | SSS | SANTOSH JADHAV | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 0.5 | 1 |  | 3
583 | NGAL09 | IDMH101630 | DG | ID_AMRAVATI | 458224 | NANDGAON PETH | AKOLA | SAI | BHUSHAN BAREKAR | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required |  | 2 |  | 1 | 2
584 | KOL152 | INMHVF3114 | NON DG | ID_KOLHAPUR | 565911 | CPR HOSPITAL | KOLHAPUR | SSS | RITESH RANGOLE | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
585 | NGPR54 | IDMH101651 | DG | ID_NAGPUR | 464807 | AMBAZARI ORDINANCE FACTORY | NAGPUR | SAI | KAILASH POKALE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 1.5 | 1.5 |  |  | 2
586 | NGP464 | INMH408259 | NON DG | ID_NAGPUR | 572725 | GADDIGUDAM CHOWK | NAGPUR | SAI | LEELADHAR BHOSKAR | SMPS | RM Faulty | RM replaced | Reopen | 2025-03-31 |  |  | 1 | 3 | 2
587 | UDGR02 | IDMH101666 | DG | ID_SOLAPUR | 505188 | UDGIR I | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-03-10 | 0.5 | 0.5 |  |  | 2
588 | GOND26 | INMH407147 | NON DG | ID_CHANDRAPUR | 501006 | LOHIA WARD | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
589 | CHRP01 | INMH408163 | DG | ID_NASHIK | 526130 | JATEGAONBK_USO | NASHIK | ATS | MANOJ SINHA | SMPS | LVD Faulty,Voltage Drop 2 Volt | Plan for SMPS STS | Open | 2025-05-30 | 1.5 |  |  |  | 1
590 | NGP395 | INMH406792 | DG | ID_NAGPUR | 565373 | BAGADGANJ | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Controller faulty | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
591 | WRNA06 | INMHVF6367 | DG | ID_KOLHAPUR | 532414 | WARNA NAGAR-2 | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS LVD and DCEM Faulty TT NO 250308CM3118685 | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  | 0.5 |  | 2
592 | PUNE37 | IDMH104534 | NON DG | ID_PUNESOUTH | 459143 | VITTHAL SMRITI, NANAPETH | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
593 | NAND63 | IDMH110415 | DG | ID_NANDED | 522836 | HUDCO EXTENTION-NANDED | LATUR | PTPL | Vacant CE Latur | SMPS | Lvd fault | SMPS replaced | Closed | 2025-04-24 | 1 | 0.5 | 0.5 |  | 3
594 | NDBR11 | IDMH108254 | DG | ID_NASHIK | 566334 | NANDURBAR CITY | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
595 | SLBZ01 | IDMH101737 | DG | ID_AMRAVATI | 458409 | SELU BAZAR | AKOLA | SAI | ALI SHAH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 1 |  |  | 1
596 | SMWB01 | IDMH109774 | DG | ID_NASHIK | 528623 | SOMAWAL BK_NEW | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 |  | 1.5 | 0.5 |  | 2
597 | ARVI01 | IDMH100092 | DG | ID_NAGPUR | 458263 | ARVI | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS Obsolute model | New SMPS Req | Open | 2025-05-30 |  | 0.5 |  |  | 1
598 | KALI01 | IDMH101758 | DG | ID_AMRAVATI | 460186 | KALI (DAU) | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Smps Controller Faulty | SMPS replaced | Closed | 2025-04-24 | 0.5 |  |  |  | 1
599 | DNCH01 | IDMH103006 | DG | ID_NASHIK | 458163 | DONDAICHA | NASHIK | ATS | NILESH BHAVSAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-04-09 |  | 0.5 |  | 1 | 2
600 | SNGV01 | IDMH103561 | DG | ID_NASHIK | 458031 | SANGVI | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
601 | VKHR01 | IDMH104351 | DG | ID_NASHIK | 458234 | VIKHRAM | NASHIK | ATS | NILESH BHAVSAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
602 | NDBR12 | IDMH108935 | DG | ID_NASHIK | 523300 | NANDUR_C | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 0.5 | 0.5 |  | 3
603 | KAKI01 | IDMH109301 | DG | ID_NASHIK | 525902 | KHADKI_USO | NASHIK | ATS | NILESH BHAVSAR | SMPS | LVD Fautly | SMPS Rectification Require | Open | 2025-05-15 | 2.5 | 2 |  |  | 2
604 | MDKD01 | IDMH101803 | DG | ID_AKOLA | 458313 | MADAKHED | AKOLA | SAI | RANJEET KAPSE | BB | BB Backup low | Plan for replacement | Open | 2025-04-30 |  |  | 1 |  | 1
605 | SIDE01 | IDMH110875 | DG | ID_NASHIK | 465655 | SHINDE | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-04-09 |  | 1.5 |  | 2 | 2
606 | BTWD01 | IDMH112424 | DG | ID_NASHIK | 457994 | BETAVAD | NASHIK | ATS | NILESH BHAVSAR | SMPS | LVD faulty, | SMPS Rectification Require | Open | 2025-05-22 |  | 1.5 |  |  | 1
607 | ANAR01 | INMH002262 | DG | ID_NASHIK | 507031 | ADRATGAON | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-03-03 | 0.5 | 1.5 | 1 |  | 3
608 | TLDA02 | IDMH111105 | NON DG | ID_NASHIK | 529421 | TALODA FL_NEW01 | NASHIK | ATS | NILESH BHAVSAR | SMPS | LVD faulty,BB Low | New BB installed lvd rectification done | Closed | 2025-04-24 | 1.5 | 4 |  | 1 | 3
609 | ANGR51 | IDMH108186 | DG | ID_AHMEDNAGAR | 565503 | SHIV ROAD, MEHERABAD | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | Low Backup BB agieng fy 2016 & Delta controller faulty | Plan for SMPS rectification & BB Replacment | Open | 2025-04-30 | 0.5 | 0.5 |  |  | 2
610 | NGP266 | IDMH108732 | DG | ID_NAGPUR | 532953 | RENUKA VIHAR COLONY | NAGPUR | SAI | MILIND RAMTEKE | SMPS | smps controller faulty | Plan for rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
611 | KKDT01 | IDMH101840 | DG | ID_AMRAVATI | 460323 | KAKADATTI | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
612 | ARDP02 | IDMH108468 | DG | ID_NANDED | 552865 | ARDHAPUR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-04-24 | 0.5 |  |  | 1 | 2
613 | AHGN02 | INMH003446 | DG | ID_SATARA | 505116 | SANGOLA (MANGALWEDHA - ANDHALGAON) | SOLAPUR | PTPL | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
614 | CAKR01 | IDMH101852 | DG | ID_NANDED | 459354 | CHAKUR | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-04-09 | 0.5 | 0.5 |  | 2 | 3
615 | NAND30 | IDMH101135 | DG | ID_NANDED | 459839 | NANKAWADI | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 |  |  | 1
616 | BMLI01 | IDMH101752 | DG | ID_SOLAPUR | 458886 | BEMLI | SOLAPUR | SAI | ROHIT GHOLAP | BB | BB Cell faulty | Plan for cell replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
617 | YSGN01 | IDMH104550 | DG | ID_AHMEDNAGAR | 565979 | OPEN PLOT KHIRDI, YESHGAON | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 1.5 |  |  |  | 1
618 | NANG01 | IDMH107195 | DG | ID_RAIGARH | 459573 | NANDGAON | PUNE-2 | ATS | AMAY DORUGADE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
619 | PNPR22 | INMHVF4365 | NON DG | ID_SATARA | 451546 | DATTAGHAT_VF | SOLAPUR | PTPL | CHANDRAKANT ANGADI | SMPS | SMPS Back panal faulty | SMPS rectification done | Closed | 2025-04-09 | 0.5 |  |  | 1 | 2
620 | PLGN06 | INMH407193 | DG | ID_NAGPUR | 451570 | PULGAON2_VF | NAGPUR | SAI | VIVEK GANJARE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 | 0.5 | 4.5 |  |  | 2
621 | PAJM04 | IDMH105671 | NON DG(MSC Sharing) | ID_GOA | 461385 | MATHIAS BUNGLOW (MSC) | GOA | SSS | SURAJ PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
622 | MNGL07 | INMH408645 | DG | ID_SOLAPUR | 585877 | killa Bhag | SOLAPUR | PTPL | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
623 | HINJ49 | IDMH107754 | NON DG | ID_PUNESOUTH | 459048 | TCS A1 BLDG (IBS) | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
624 | SHRD01 | IDMH103162 | DG | ID_NASHIK | 458227 | SHIRUD | NASHIK | ATS | SWAPNIL SALWE | BB | BB Backup low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
625 | LMKN01 | IDMH103377 | DG | ID_NASHIK | 458083 | LAMKANI | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
626 | HIN105 | INMH005519 | NON DG | ID_PUNESOUTH | 451347 | EMCURE_VF2_W3G | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Cable | RRU in Critical & Voltage Drop SMPS to RRU | Load shifted on non critical - 5-Sep & VIL to replace cable | Open | VIL Support Required | 0.5 |  | 0.5 |  | 2
627 | NAND11 | IDMH102088 | DG | ID_NANDED | 460289 | TARODA KHURD | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 1 |  | 1 | 2
628 | NAND06 | IDMH112098 | DG | ID_NANDED | 565363 | SARAFA BAZAR_NANDED | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
629 | KUND01 | IDMH103262 | DG | ID_NANDED | 459555 | KUNDALWADI | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
630 | NAND25 | IDMH107084 | DG | ID_NANDED | 522939 | SHIVAJI NAGAR, NANDED (RELOCATION) | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-04-24 | 1 |  | 1 |  | 2
631 | AMVT91 | INMH407762 | DG | ID_AMRAVATI | 566202 | LIC HEADQUARTERS | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
632 | ANJN01 | IDMH102305 | DG | ID_AMRAVATI | 457991 | ANJANGAON | AKOLA | SAI | BHUSHAN BAREKAR | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
633 | CNPR01 | IDMH103869 | DG | ID_AHMEDNAGAR | 505250 | CHANDANAPURI | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 1 |  |  | 1
634 | BRDD01 | IDMH104017 | DG | ID_NASHIK | 458305 | BORAD | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS LVD faulty | SMPS rectification done | Reopen | 2025-02-15 | 2 | 0.5 |  | 8 | 3
635 | NAND16 | IDMH106534 | DG | ID_NANDED | 505097 | GANESHNAGAR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Faulty | SMPS rectification done | Closed | 2025-04-24 |  |  | 1 | 1 | 2
636 | KTHD01 | IDMH101819 | DG | ID_CHANDRAPUR | 451418 | KOTHODA BK. | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller and DCIF card faulty | SMPS complaint open, Quotation awaited | Open | 2025-05-15 | 0.5 | 1 |  |  | 2
637 | WANI05 | IDMH108689 | DG | ID_CHANDRAPUR | 565749 | WANI | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
638 | DULE68 | INMH405744 | NON DG | ID_NASHIK | 595027 | Mulla Nagar_Airtel | NASHIK | ATS | SWAPNIL SALWE | SMPS | SMPS Controller faulty | SPMS Rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
639 | MASA01 | IDMH101960 | DG | ID_SOLAPUR | 459402 | MASSA | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
640 | NIGN01 | IDMH107472 | DG | ID_NANDED | 505163 | NAIGAON BAZAR | LATUR | PTPL | RAJKUMAR ALANE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-31 | 3 | 2 | 0.5 |  | 3
641 | AMVT27 | IDMH111378 | DG | ID_AMRAVATI | 566204 | MIDC AMRAVATI | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 | 1 |  |  |  | 1
642 | PUN187 | IDMH105061 | DG | ID_PUNENORTH | 458772 | AJMERA COLONY | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
643 | RNPR01 | IDMH102081 | DG | ID_SOLAPUR | 459310 | RENAPUR | LATUR | SAI | SUDHIR AGHE | SMPS | Smps Lvd Faulty | SMPS replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
644 | PALI01 | IDMH101830 | DG | ID_RAIGARH | 505451 | PALI - 2 | PUNE-3 | ATS | ANANT TIDKE | BB | BB Backup Very Low | BB upgradation done | Closed | 2025-03-31 | 0.5 | 3 |  |  | 2
645 | SHHR01 | IDMH107797 | DG | ID_RAIGARH | 458674 | SHAHPUR | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS BER | SMPS replaced | Closed | 2025-04-09 | 1 | 1.5 |  | 2 | 3
646 | PUN409 | IDMH106601 | DG | ID_PUNENORTH | 458733 | NEW SANGHVI II | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
647 | AURN97 | IDMH102064 | DG | ID_AURANGABAD | 566067 | Â KRISHI VIDYAPEETH | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
648 | CHKN43 | IDMH108363 | DG | ID_PUNENORTH | 523330 | MOEE_PUNE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  | 0.5 | 1 | 3
649 | CHKN42 | IDMH108422 | DG | ID_PUNENORTH | 523534 | TETRA PACK PUNE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  | 1 | 2
650 | MKPR12 | INMH404289 | DG | ID_AKOLA | 524934 | PARPET AREA_NEW | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-04-09 | 0.5 | 0.5 | 0.5 | 2 | 4
651 | SHRA11 | IDMH110803 | NON DG | ID_RAIGARH | 529896 | AAMBY VALLEY NORTH LAKE | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-28 | 0.5 | 1 |  |  | 2
652 | GUGI01 | IDMH102113 | DG | ID_SOLAPUR | 458693 | GHUGGI | SOLAPUR | SAI | ROHIT GHOLAP | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
653 | AKLT07 | IDMH110711 | DG | ID_SOLAPUR | 502736 | AKKALKOT STN ROAD | SOLAPUR | PTPL | SATYASHIL PATIL | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
654 | MLCH01 | IDMH103581 | DG | ID_AHMEDNAGAR | 459894 | MALICHINCHORA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | RRU | RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
655 | NAND47 | IDMH108688 | DG | ID_NANDED | 574477 | VISHAL NAGAR | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-04-09 |  | 0.5 | 0.5 | 1 | 3
656 | AJPR02 | INMH005298 | DG | ID_NANDED | 507045 | ARZAPUR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
657 | PUSS01 | IDMH102203 | DG | ID_AHMEDNAGAR | 459723 | PUS | LATUR | PTPL | ASHWIN KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
658 | MNGI01 | IDMH101944 | DG | ID_AHMEDNAGAR | 464833 | MUNGI | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | BB replaced | Closed | 2025-02-07 |  | 0.5 |  |  | 1
659 | DBRN01 | IDMH103848 | DG | ID_AKOLA | 457992 | DAMBHURNI | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
660 | ARDP04 | INMH405770 | NON DG | ID_NANDED | 586346 | Airtel_ARDHAPUR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | Smps Controller And Lvd Faulty | RM & Controller requited | Open | 2025-04-20 | 0.5 | 1 |  | 4 | 3
661 | MNSH01 | IDMH101094 | DG | ID_AMRAVATI | 505318 | MUND NILKANTH SAKHARAM | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
662 | GWDN01 | IDMH101425 | DG | ID_AMRAVATI | 460395 | GOWARDHAN | AKOLA | SAI | ALI SHAH | SMPS | Delat SMPS BLVD. LVD RM backplane and controller faulty | SMPS Rectification require | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
663 | ABGC01 | IDMH105273 | NON DG | ID_RAIGARH | 459497 | HI-TECH CARBON | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  |  | 1
664 | SHRA04 | IDMH106067 | DG | ID_RAIGARH | 507050 | ESSAR AGROTECH | PUNE-3 | ATS | PRATIK HULAVALE | BB | BB Theft from site | BB install | Closed | 2025-04-24 | 1.5 | 1 | 1 | 1 | 4
665 | TTPI01 | IDMH102281 | DG | ID_AURANGABAD | 464912 | TATTEWADI | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
666 | TAND01 | IDMH102294 | DG | ID_SATARA | 459751 | TANDULWADI | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | Smps Lvd Faulty | SMPS rectification done | Closed | 2025-04-24 | 1.5 | 0.5 | 0.5 |  | 3
667 | HAGN01 | IDMH103156 | DG | ID_AHMEDNAGAR | 505476 | HATGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | RRU | RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 |  |  | 1
668 | MAKA01 | IDMH103259 | DG | ID_AHMEDNAGAR | 460103 | MAKA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | BB replaced | Closed | 2025-01-04 | 0.5 |  |  |  | 1
669 | MKPR03 | IDMH102440 | DG | ID_AKOLA | 458044 | BULDHANA ROAD | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 |  |  | 1 |  | 1
670 | USMD05 | IDMH102334 | DG | ID_SOLAPUR | 458830 | SOLAPUR ROAD | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
671 | DSBD01 | IDMH101892 | DG | ID_AKOLA | 460061 | DUSARBID | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | VIL Support require | Open | VIL Support Required | 4.5 | 1.5 | 0.5 | 1 | 4
672 | SLTN01 | IDMH101995 | DG | ID_AKOLA | 459844 | SULTANPURA | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 |  | 0.5 |  | 2
673 | MLBA01 | IDMH102271 | DG | ID_SOLAPUR | 459471 | MALUMBRA | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
674 | AWAR01 | IDMH102125 | DG | ID_AKOLA | 458006 | AWAR | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | Support req | Open | VIL Support Required |  | 0.5 |  |  | 1
675 | NGSR01 | IDMH101970 | DG | ID_SOLAPUR | 459290 | NAGANSUR | SOLAPUR | SAI | SATYASHIL PATIL | BB | BB Cell faulty | Plan for cell replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
676 | LPEN08 | INMH401597 | DG | ID_RAIGARH | 570449 | RAMWADI | PUNE-3 | ATS | ANANT TIDKE | RRU | RRU Faulty | RRU rectification done | Closed | 2025-01-31 | 0.5 |  |  |  | 1
677 | BLPG01 | IDMH103741 | DG | ID_AHMEDNAGAR | 460241 | BELPIMPALGAON | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | BB Theft | BB install | Closed | 2025-05-30 |  | 0.5 |  |  | 1
678 | PU2476 | INMH405340 | NON DG | ID_PUNESOUTH | 587219 | Autadewadi Lake | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  | 1 | 2
679 | AMV125 | INMH405768 | NON DG | ID_AMRAVATI | 594156 | Gopal Nagar Amravati | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Smps Controller Faulty | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
680 | DUDA01 | IDMH102662 | DG | ID_AKOLA | 458553 | DUDHA | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
681 | DOMA01 | IDMH100013 | DG | ID_CHANDRAPUR | 451487 | DOMA_V_USO | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Faulty | SMPS rectification done | Closed | 2025-03-07 | 0.5 |  | 0.5 |  | 2
682 | KOLI01 | IDMH103066 | DG | ID_AKOLA | 458395 | KOTHALI | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-15 | 1 |  | 0.5 | 2 | 3
683 | PGDL01 | IDMH102688 | DG | ID_AKOLA | 460204 | PANGRADOLE | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 1 |  |  | 1
684 | UMRD04 | IDMH108129 | DG | ID_NAGPUR | 567141 | ADYALWALE LE-OUT | NAGPUR | SAI | BEERENDRA SINGH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
685 | DUDR01 | IDMH109702 | DG | ID_RAIGARH | 525441 | DUNDRE_USO | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending | 2 | 2.5 |  | 2 | 3
686 | JALB01 | IDMH102519 | DG | ID_AKOLA | 458109 | JALAMB | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 | 4 |  | 0.5 |  | 2
687 | SWOT01 | IDMH112177 | DG | ID_AHMEDNAGAR | 528026 | SAWARGAON GHAT | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 | 1 |  |  |  | 1
688 | SNKR01 | IDMH103180 | DG | ID_AKOLA | 460141 | SINDKHED RAJA | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
689 | PGRI01 | IDMH102539 | DG | ID_SOLAPUR | 507079 | PANGRI | SOLAPUR | PTPL | ROHIT GHOLAP | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
690 | KHAM01 | IDMH103548 | DG | ID_AKOLA | 458299 | GOPI SADAN | AKOLA | SAI | RANJEET KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
691 | CHRG01 | IDMH111433 | DG | ID_CHANDRAPUR | 451261 | CHARGAONKH_USO_V | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 1 |  | 0.5 |  | 2
692 | PU2339 | INMH408026 | NON DG | ID_PUNENORTH | 451556 | KROMEMALL_VF | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  | 2 |  |  | 1
693 | MUST01 | IDMH103852 | DG | ID_SOLAPUR | 459688 | MUSTI | SOLAPUR | SAI | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  |  | 1
694 | BRSI01 | IDMH102587 | DG | ID_SOLAPUR | 458619 | MAHATMA GANDHI SHOPPING CMPLX | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | Smps Lvd Faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
695 | WRDH21 | IDMH107815 | DG | ID_NAGPUR | 565967 | NEAR HANUMAN MANDIR, ALODI | NAGPUR | SAI | VIVEK GANJARE | RRU | RRU faulty | RRU rectification done | Closed | 2025-03-31 | 1 |  | 1 | 3 | 3
696 | BTBR04 | IDMH109185 | NON DG | ID_NAGPUR | 458002 | INDORAMA SYNTHETIC | NAGPUR | INHOUSE | VIVEK GANJARE | RRU | 1 RRU Faulty | RRU replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
697 | DTBJ01 | IDMH108479 | DG | ID_AKOLA | 523976 | DHITRA BHANGOJI_NEW | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Controller faulty | SMPS rectification done | Reopen | 2025-03-31 | 1.5 | 1.5 | 0.5 | 1 | 4
698 | GVDP01 | IDMH100283 | DG | ID_CHANDRAPUR | 451351 | GOVINDPUR_V_USO | NAGPUR | SAI | BEERENDRA SINGH | SMPS | PP conroller faulty & low backup, 2 cell faulty | PP ro replaced & R&R BB required | Open | 2025-05-15 |  | 2 | 1.5 |  | 2
699 | GJTI01 | IDMH102611 | DG | ID_SOLAPUR | 459630 | GUNJOTI | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
700 | GJNR01 | IDMH103458 | NON DG | ID_AKOLA | 458406 | GAJANAN NAGAR | AKOLA | SAI | RANJEET KAPSE | SMPS | RM faulty | RM replaced | Closed | 2025-03-31 |  | 1 |  |  | 1
701 | DRWA01 | IDMH102630 | DG | ID_AMRAVATI | 464937 | DARWHA | AKOLA | SAI | DHANRAJ NIBALKAR | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 0.5 | 2 |  | 2 | 3
702 | KHAM20 | INMH004190 | DG | ID_AKOLA | 505538 | BOBDEY COLONY | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
703 | BDNR09 | INMH408590 | DG | ID_AMRAVATI | 565848 | BADNERA OLD CITY | AKOLA | NonActive | BHUSHAN BAREKAR | RRU | RRU Faulty | Support req | Open | VIL Support Required |  | 2 | 2 | 10 | 3
704 | DMGN05 | INMH408142 | DG | ID_AMRAVATI | 565319 | DHAMANGAON | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  | 3 | 2
705 | KHAD01 | IDMH111425 | DG | ID_AMRAVATI | 458165 | KHED | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
706 | KDER01 | IDMH103155 | DG | ID_SOLAPUR | 459636 | KADER | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Backplane Faulty | SMPS Rectification Done | Closed | 2025-03-31 |  |  | 0.5 |  | 1
707 | DOKI01 | IDMH103599 | DG | ID_SOLAPUR | 565636 | DHOKITERANA NGR | SOLAPUR | PTPL | ROHIT GHOLAP | Cable | SMPS to DCDB Underated cable & Voltage drop > 3 V | cable to replace | Open | 2025-04-20 |  | 0.5 |  |  | 1
708 | PUN770 | IDMH105882 | DG | ID_PUNENORTH | 500957 | PIMPRI WAGHIRE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
709 | USMD04 | IDMH107135 | DG | ID_SOLAPUR | 459359 | OSMANABAD R-BSC | SOLAPUR | SAI | ROHIT GHOLAP | Cable | DCDB to RRU Underrated cable vtg drop 3v | Cable replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
710 | WGLA01 | IDMH102695 | DG | ID_AHMEDNAGAR | 458817 | WAGHALA | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-05-22 |  | 1 |  |  | 1
711 | LNVL13 | IDMH107658 | NON DG | ID_RAIGARH | 459611 | DELLA ENCLAVE | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS controller Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 1 | 0.5 |  | 3
712 | BTBR03 | IDMH110074 | DG | ID_NAGPUR | 531372 | BUTIBORI 3 | NAGPUR | SAI | VIVEK GANJARE | RRU | RRU faulty | RRU rectification done | Closed | 2025-04-24 | 0.5 | 0.5 |  | 16 | 3
713 | BRMT34 | IDMH103543 | NON DG | ID_PUNESOUTH | 458625 | IMSOFER_COW | PUNE-1 | INHOUSE | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
714 | BHSE01 | IDMH102720 | DG | ID_SATARA | 459582 | BHOSE | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Back panal faulty | SMPS rectification done | Closed | 2025-02-28 | 1 | 1 |  |  | 2
715 | BLHE01 | IDMH104887 | DG | ID_RAIGARH | 460390 | BELHE | PUNE-1 | ATS | SWAPNIL KARAD | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
716 | KRKA01 | IDMH111565 | DG | ID_SOLAPUR | 459283 | KARAJKHEDA | SOLAPUR | SAI | ROHIT GHOLAP | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
717 | BTBR06 | INMH000581 | DG | ID_NAGPUR | 522528 | RUI KHAIRI | NAGPUR | SAI | VIVEK GANJARE | Load Segregation | Cable connected with Critical | DCDB Power tappping from Critical source for shifting PE required Will closed soon | Open | 2025-04-20 |  |  | 1.5 | 2 | 2
718 | LNER01 | IDMH101514 | DG | ID_AMRAVATI | 565311 | NER PARSOPANT | AKOLA | SAI | DHANRAJ NIBALKAR | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required |  | 0.5 |  |  | 1
719 | KHNK01 | IDMH108654 | DG | ID_AKOLA | 523897 | KINHI NAIK | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
720 | KRJT02 | IDMH106708 | DG | ID_RAIGARH | 464876 | MAHAVEER PETH | PUNE-3 | ATS | ANANT TIDKE | BB | Low Battery Backup | BB replaced | Closed | 2025-02-15 | 2 |  |  |  | 1
721 | YAVT05 | IDMH100281 | DG | ID_AMRAVATI | 458608 | BANGADE NAGAR | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  | 0.5 |  | 2
722 | PKBK01 | IDMH102987 | DG | ID_SATARA | 459435 | PACHEGAON | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
723 | DYPR01 | IDMH102800 | DG | ID_AMRAVATI | 457974 | DARYAPUR | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Smps Controller Faulty | SMPS rectification done | Closed | 2025-03-31 |  |  | 1 |  | 1
724 | TDGN01 | IDMH102807 | DG | ID_AURANGABAD | 460376 | TADHATGAON | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
725 | BRLN01 | IDMH102810 | DG | ID_SATARA | 458876 | BARLONI | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | SMPS LVD FAULTY | LVd rectification plan | Open | 2025-05-22 |  | 0.5 |  |  | 1
726 | MAND01 | IDMH103063 | DG | ID_SATARA | 459536 | MANDAVE | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
727 | WLKI01 | IDMH103357 | DG | ID_AHMEDNAGAR | 460056 | WALKI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
728 | SWNA01 | IDMH101229 | DG | ID_AMRAVATI | 459825 | SAWANA | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | LVD Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  |  |  | 1
729 | GTND01 | IDMH102819 | DG | ID_PUNESOUTH | 458999 | GOTANDI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-15 |  | 0.5 | 1 | 1 | 3
730 | MNPR01 | IDMH103716 | DG | ID_SATARA | 459628 | MENDHAPUR | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
731 | RMTK01 | IDMH101606 | DG | ID_NAGPUR | 458099 | RAMTEK | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU Faulty | RRU replaced | Closed | 2025-03-31 |  |  | 1.5 | 1 | 2
732 | TKLI01 | IDMH104472 | DG | ID_SOLAPUR | 458718 | TAKALI | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
733 | BHWL02 | IDMH102852 | DG | ID_AKOLA | 458170 | BHUSAWAL (2) | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | Controller Faulty | Plan for rectification | Open | 2025-04-30 |  |  | 3 |  | 1
734 | NGPR85 | IDMH101148 | DG | ID_NAGPUR | 464899 | ISHWAR NAGAR | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
735 | MHLG01 | IDMH100587 | DG | ID_NAGPUR | 458041 | MAHALGAON | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-20 | 0.5 | 1 |  | 2 | 3
736 | SIPR02 | IDMH103860 | DG | ID_NASHIK | 505099 | SHIRPUR | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-15 |  | 1 |  |  | 1
737 | NSK375 | INMH404287 | DG | ID_NASHIK | 529088 | KEWAL PARK_NASHIK | NASHIK | ATS | SUBHASH SHINDE | BB | BB cell faulty | Plan for cell replacement | Open | 2025-04-30 | 1 |  |  |  | 1
738 | NGPR68 | IDMH101208 | DG | ID_NAGPUR | 565382 | DINGRI KHURD - RING RD | NAGPUR | SAI | MILIND RAMTEKE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-04-24 | 1.5 | 0.5 | 1 | 3 | 4
739 | PU2259 | INMH407986 | NON DG | ID_PUNENORTH | 451533 | AMANORA_TWR8_VF | PUNE-1 | INHOUSE | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 1 |  | 0.5 |  | 2
740 | MODA02 | IDMH112128 | DG | ID_NAGPUR | 567151 | MOUDA | NAGPUR | SAI | MILIND RAMTEKE | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  | 1 | 2
741 | KONS01 | IDMH100355 | DG | ID_CHANDRAPUR | 451417 | KONSARI | NAGPUR | SAI | BEERENDRA SINGH | BB | BB Backup low | Plan for BB upgradation | Open | 2025-04-30 | 1 | 1 | 0.5 |  | 3
742 | BHDU02 | INMH408362 | DG | ID_NAGPUR | 531361 | VIHIRGAON | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS RM faulty | RM replaced | Closed | 2025-02-28 |  | 2 |  |  | 1
743 | SRWL01 | IDMH104394 | DG | ID_SATARA | 565492 | SHIRWAL | PUNE-2 | ATS | RAHUL TUPARE | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-02-05 | 1 | 0.5 |  |  | 2
744 | CPTL01 | IDMH102951 | DG | ID_AHMEDNAGAR | 505309 | CHICHONDI PATIL | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS Controller faulty | New SMPS installed | Closed | 2025-01-30 | 1.5 |  |  |  | 1
745 | NAON01 | IDMH100236 | DG | ID_CHANDRAPUR | 451256 | NIMGAON | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Faulty | Planned for SMPS rectification | Open | 2025-05-15 | 0.5 | 1 |  |  | 2
746 | DULE41 | IDMH112353 | DG | ID_NASHIK | 529260 | SHRI BHAUSAHEB HIRE GOVERNMENT MEDICAL COLLEGE | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
747 | CHMR03 | IDMH111311 | DG | ID_CHANDRAPUR | 567150 | CHIMOOR | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-31 | 1 | 2.5 | 1 |  | 3
748 | DMGN01 | IDMH101589 | DG | ID_AMRAVATI | 458135 | DHAMANGAON RAILWAY | AKOLA | SAI | BHUSHAN BAREKAR | BB | Battery backup very low | BB replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
749 | LMBR01 | IDMH100353 | DG | ID_CHANDRAPUR | 451266 | LAKHAMAPURBORI_USO_V | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
750 | AURD01 | IDMH101617 | DG | ID_SOLAPUR | 459285 | AURAD SHAHAJANI | LATUR | SAI | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 1.5 |  |  | 1
751 | LAUL01 | IDMH104392 | DG | ID_SATARA | 459286 | LAUL | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | CONTROLLER FAULTY | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
752 | CHKN27 | IDMH106337 | DG | ID_PUNENORTH | 502951 | MAHINDRA PROJECT | PUNE-3 | ATS | Vacant CE Pune-3 | BB | BB Backup low | BB replaced | Closed | 2025-04-24 | 1.5 | 3 | 1 |  | 3
753 | BLMN01 | IDMH106566 | DG | ID_RAIGARH | 570212 | BORLI MANDALA | PUNE-2 | ATS | AMAY DORUGADE | RRU | 1-RRU Malfunctiong | VIL to rectify | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
754 | PUNE55 | IDMH105240 | DG | ID_PUNESOUTH | 459171 | SAI KRIPA, SAHAKAR NAGAR | PUNE-2 | ATS | RAHUL TUPARE | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-22 | 1.5 |  |  |  | 1
755 | ANGR09 | IDMH103030 | NON DG | ID_AHMEDNAGAR | 460352 | OLD CLOTH MARKET | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS Faulty | SMPS Replaced | Closed | 2025-02-09 | 0.5 | 0.5 |  |  | 2
756 | SAWG01 | INMH000194 | DG | ID_CHANDRAPUR | 451255 | SAWARGAON2_V_USO | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
757 | PU2148 | INMH003116 | NON DG | ID_PUNENORTH | 451304 | MEGAMART_ENT_VF | PUNE-3 | ATS | Vacant CE Pune-3 | Cable | DCDB To RRU drop 3V drop | VIL to replace cable | Open | VIL Support Required | 0.5 | 0.5 | 0.5 |  | 3
758 | NAND92 | INMH408631 | NON DG | ID_NANDED | 507129 | SANDEEPANI PUBLIC SCHOOL (BALAJI NAGAR) | LATUR | NonActive | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 1 |  |  | 1
759 | HINJ15 | IDMH105141 | NON DG | ID_PUNESOUTH | 459045 | INFOSYS PHASE(II) HINJEWADI | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Cable | DCDB To RRU drop 5V drop | VIL to replace cable | Open | VIL Support Required | 3 | 2 | 1.5 | 1 | 4
760 | DUND04 | IDMH103054 | DG | ID_PUNESOUTH | 505497 | SANSKAR NAGAR (DAUND) | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | Smps Controller Faulty | SMPS replaced | Closed | 2025-04-09 | 0.5 |  |  | 1 | 2
761 | NGPR78 | IDMH100917 | DG | ID_NAGPUR | 565391 | WADI_CHINTAMANI_AIRTELSHARING | NAGPUR | SAI | KAILASH POKALE | Cable | Voltage drop more due to Shelter & BTS distance 30 Mtrs | Power Cable upgradation Require | Open | VIL Support Required | 0.5 |  |  | 1 | 2
762 | MTGN01 | IDMH100859 | DG | ID_CHANDRAPUR | 451486 | MOTEGAON_V_USO | NAGPUR | SAI | BEERENDRA SINGH | SMPS | Controller Alarm Card Faulty | Plan for rectification | Open | 2025-04-30 |  | 1.5 |  |  | 1
763 | PU1174 | IDMH110395 | DG | ID_PUNENORTH | 527670 | MORE WASTI | PUNE-3 | ATS | Vacant CE Pune-3 | Cable | SMPS To RRU drop 3V drop | VIL to replace cable | Open | VIL Support Required | 1 | 2 | 2.5 |  | 3
764 | PU1232 | IDMH106390 | DG | ID_PUNENORTH | 527899 | KATE VASTI, PUNAWALE. | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Cable | DCDB To RRU drop 3V drop | VIL to replace cable | Open | VIL Support Required | 1 |  |  |  | 1
765 | WDOD01 | IDMH101696 | DG | ID_AKOLA | 464808 | WADODA | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-22 | 2.5 |  |  |  | 1
766 | NDGN02 | IDMH105931 | DG | ID_NASHIK | 566801 | OPEN PLOT NANDGAOAN | NASHIK | ATS | Vacant Vacant CE Nashik | Cable | SMPS to RRU Cable Under Rated Cable ,Voltge Drop 4 Volt on BB Due to SMPS to VIL Chiller 16 Sq MM Cable-15 Mtr,VIL Chiller to RRU 6 SQ MM -50 Mtr. | Cable Replacement Require | Open | VIL Support Required | 1 |  |  |  | 1
767 | MSRL01 | IDMH102275 | DG | ID_AKOLA | 505491 | MASRUL | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 |  |  |  | 1
768 | NSK190 | IDMH106999 | DG | ID_NASHIK | 567065 | SAVTA NAGAR | NASHIK | ATS | SUBHASH SHINDE | Cable | SMPS to DCDB 6 Sq MM Cable used-6 Mtr Each , High voltage drop | SMPS to DCDB Cable Replacement Require | Open | 2025-04-20 | 0.5 |  |  |  | 1
769 | KOND01 | IDMH102150 | DG | ID_SOLAPUR | 459686 | KONDI | SOLAPUR | SAI | BALASAHEB KADAM | Cable | DCDB to RRU Drop > 3 V | VIL to Replace cable | Open | VIL Support Required | 0.5 |  |  |  | 1
770 | MICR01 | INMH403769 | NON DG | ID_PUNESOUTH | 464919 | IDEA OFFICE | PUNE-2 | INHOUSE | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
771 | PU1982 | INMH000577 | NON DG | ID_PUNESOUTH | 526260 | KOTHRUD CORNER | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
772 | SAVA01 | INMH002264 | DG | ID_AKOLA | 505181 | SAVKHEDA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Cable | Charging Mode Voltage Drop 3 Volt & DisCharging Mode Voltage Drop 4 Volt,Cable 6 Sq MM | VIL Cable Replacement Require,LVD Setting Changed 44 To 45 Volt,PE & DCDB Require | Open | VIL Support Required |  | 1 |  |  | 1
773 | PUN851 | IDMH107574 | DG | ID_PUNESOUTH | 522085 | PUNE UNIVERSITY 02- ADMINISTRATION BUILDING | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
774 | PU2009 | IDMH109814 | NON DG | ID_PUNESOUTH | 574627 | OMEGA HERITAGE | PUNE-2 | ATS | AKSHAY SHELAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
775 | MUDZ01 | IDMH112369 | DG | ID_CHANDRAPUR | 451425 | MUDZA | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Controller faulty | Controller to be replaced | Open | 2025-04-30 | 0.5 |  |  |  | 1
776 | PUN473 | IDMH103913 | NON DG | ID_PUNESOUTH | 459084 | PANCHELI CHOWK | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 2 |  | 1
777 | BHMP01 | IDMH100011 | DG | ID_CHANDRAPUR | 458005 | BRAHMPURI | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 2.5 |  | 0.5 | 1 | 3
778 | SDSS01 | IDMH100021 | DG | ID_SATARA | 465850 | SANTH DAMAJEE SUGAR FACTORY | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS controller faulty | Planned for SMPS rectification | Open | 2025-05-07 | 1 | 1.5 | 1 |  | 3
779 | PURA01 | IDMH110013 | DG | ID_CHANDRAPUR | 523943 | PURADA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Cable | SMPS to Transmissin Rack cable underrated | Plan for cable replacement | Open | 2025-04-20 | 8.5 | 9.5 | 10 | 9 | 4
780 | MGNW01 | IDMH103354 | DG | ID_AKOLA | 458410 | MANGRUR NAWGHARE | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
781 | AHTI01 | IDMH100072 | DG | ID_CHANDRAPUR | 460154 | ASHTI | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 1 |  |  | 1
782 | NGPR11 | IDMH100079 | DG | ID_NAGPUR | 458357 | GANGOTRI | NAGPUR | SAI | MILIND RAMTEKE | RRU | RRU faulty | Support req | Open | VIL Support Required |  | 0.5 |  |  | 1
783 | PUN149 | IDMH105296 | NON DG | ID_PUNESOUTH | 459190 | BALAJI NAGAR | PUNE-2 | ATS | RAHUL TUPARE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
784 | NGBD01 | IDMH100126 | DG | ID_CHANDRAPUR | 458094 | NAGBHID | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
785 | MHKR01 | IDMH103485 | DG | ID_AKOLA | 460294 | MEHEKAR | AKOLA | SAI | RANJEET KAPSE | SMPS | RM faulty | RM replaced | Closed | 2025-03-31 |  | 0.5 | 1.5 |  | 2
786 | NLGR01 | IDMH100440 | DG | ID_SOLAPUR | 459415 | NALGIR | LATUR | SAI | SUDHIR AGHE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 1 |  |  | 2
787 | PUN186 | IDMH106196 | DG | ID_PUNESOUTH | 459204 | PAUD PHATA,PUNE | PUNE-2 | ATS | AKSHAY SHELAR | BB | BB Backup very low | BB replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
788 | NGRT01 | IDMH100235 | DG | ID_CHANDRAPUR | 451269 | NAVEGAON2_V_USO | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
789 | PETD01 | IDMH100243 | DG | ID_CHANDRAPUR | 451411 | GAURIPUR/PETADA | NAGPUR | SAI | BEERENDRA SINGH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
790 | TRDA01 | IDMH100244 | DG | ID_CHANDRAPUR | 458078 | TIRODA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
791 | NPHD01 | IDMH105709 | DG | ID_NASHIK | 566559 | OPEN PLOT NIPHAD | NASHIK | ATS | Vacant Vacant CE Nashik | RRU | RRU faulty | Support req | Open | VIL Support Required | 1.5 | 0.5 | 2.5 |  | 3
792 | NGPR01 | IDMH100259 | DG | ID_NAGPUR | 458352 | DARBARI | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
793 | WHOD01 | IDMH100263 | DG | ID_NAGPUR | 458128 | WAGHODA | NAGPUR | SAI | KAILASH POKALE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
794 | PUN729 | IDMH107548 | DG | ID_PUNESOUTH | 521457 | WADGAON | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS controller faulty | Plan for SMPS replacement | Open | 2025-05-07 | 4 | 0.5 | 0.5 |  | 3
795 | PU1198 | IDMH110194 | DG | ID_PUNESOUTH | 505430 | WADGAON BK II | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
796 | NVRE01 | IDMH103359 | DG | ID_PUNENORTH | 458819 | NHAVARE | PUNE-1 | SAI | HARSHAL MAHAJAN | SMPS | SMPS Controller Faulty | SMPS rectification done | Closed | 2025-03-31 | 1 | 2 |  |  | 2
797 | MHGI01 | IDMH108078 | DG | ID_NANDED | 523974 | MAHALINGI | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
798 | CHAR01 | IDMH100287 | DG | ID_CHANDRAPUR | 460142 | CHARMOSHI | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
799 | PLJT01 | IDMH100289 | DG | ID_CHANDRAPUR | 458411 | PALASGAON JAT | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-31 | 1.5 |  |  |  | 1
800 | SUDL01 | IDMH100294 | DG | ID_CHANDRAPUR | 505333 | SAUNDAL | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
801 | PU2012 | IDMH110326 | NON DG | ID_PUNESOUTH | 577371 | AMBEGAON PATHAR(SAI | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
802 | BDRV01 | IDMH100313 | DG | ID_CHANDRAPUR | 459843 | BHADRAVATI | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
803 | PU1305 | IDMH110456 | NON DG | ID_PUNESOUTH | 575272 | PAWAR HOSPITAL BALAJ | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 | 2 | 2
804 | LATR78 | INMH405749 | NON DG | ID_SOLAPUR | 591216 | Sul Galli | LATUR | SAI | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
805 | MANJ01 | IDMH108231 | DG | ID_NANDED | 526301 | MANJARI_NANDED_USO | LATUR | PTPL | RAJKUMAR ALANE | BB | Zero Battery Backup | BB replaced | Closed | 2025-04-24 | 1 | 1.5 | 1.5 |  | 3
806 | WRTI01 | IDMH100350 | DG | ID_CHANDRAPUR | 458308 | WARTI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  | 1.5 | 1 | 3
807 | WRGD01 | IDMH100351 | DG | ID_CHANDRAPUR | 458550 | WAIRAGAD | NAGPUR | SAI | BEERENDRA SINGH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
808 | WDHA01 | IDMH100352 | DG | ID_CHANDRAPUR | 451440 | WADDHA | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS controller faulty | Plan for rectification | Open | 2025-04-20 | 1.5 | 1 | 1.5 |  | 3
809 | WANI04 | IDMH100360 | DG | ID_CHANDRAPUR | 459879 | JAIN LAYOUT | NAGPUR | SAI | GANESH DANDALWAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
810 | IJLA01 | IDMH100370 | DG | ID_NAGPUR | 458028 | INJHALA | NAGPUR | SAI | VIVEK GANJARE | Load Segregation | Baseband critical | Critical to non critical | Closed | 2025-03-31 | 0.5 |  |  |  | 1
811 | MLSL01 | IDMH108250 | DG | ID_AMRAVATI | 523893 | MALSHELU | AKOLA | SAI | ALI SHAH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 4 | 1
812 | DEWD01 | IDMH100407 | DG | ID_CHANDRAPUR | 451406 | DEWADA | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
813 | SAGM04 | IDMH103417 | DG | ID_AHMEDNAGAR | 460162 | VELHALE | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-02-16 | 1 | 0.5 |  |  | 2
814 | AWLG01 | IDMH100416 | DG | ID_CHANDRAPUR | 451352 | AWALGAON_V_USO | NAGPUR | SAI | BEERENDRA SINGH | SMPS | Backpanel Faulty / Panel Not Available | Plan for rectification | Open | 2025-05-15 | 1 |  | 0.5 |  | 2
815 | PUN108 | INMH406438 | DG | ID_PUNESOUTH | 459078 | SADASHIV PETH | PUNE-2 | NonActive | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
816 | POTG01 | IDMH100461 | DG | ID_CHANDRAPUR | 451430 | POTEGAON | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 1 |  |  |  | 1
817 | BDKN01 | IDMH103448 | DG | ID_AURANGABAD | 460091 | BIDKIN | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | RRU | RRU faulty - Replacement activity | NA | Closed | 2025-01-23 | 1 |  |  |  | 1
818 | PU1689 | INMH408167 | NON DG | ID_PUNESOUTH | 575256 | BLOOMFIELD BY AMIT ENTERPRISES HOUSING LIMITED | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
819 | MKLN01 | IDMH110066 | DG | ID_AMRAVATI | 523957 | MALEGAON NAJIK KINHI | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  | 1 | 2
820 | AMVT62 | IDMH103467 | DG | ID_AMRAVATI | 565850 | UDAY COLONY (SAI NAGAR 2) | AKOLA | SAI | BHUSHAN BAREKAR | BB | BB cell faulty | cell replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
821 | OMNT01 | IDMH100533 | DG | ID_RAIGARH | 570333 | HOTEL NATWAR SHEDUNG | PUNE-3 | ATS | ANANT TIDKE | Cable | SMPS to BTS Long distance 30m | cable distane reduction req | Open | VIL Support Required |  | 0.5 |  |  | 1
822 | NGP105 | IDMH100536 | DG | ID_NAGPUR | 458332 | AJNI SQUARE | NAGPUR | SAI | KAILASH POKALE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
823 | NGP101 | IDMH100537 | DG | ID_NAGPUR | 458335 | PANCHDEEP | NAGPUR | SAI | KAILASH POKALE | RRU | RRU Faulty | RRU replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
824 | NGPR44 | IDMH100539 | DG | ID_NAGPUR | 458379 | AJNI SQUARE | NAGPUR | SAI | KAILASH POKALE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 | 0.5 |  | 1 |  | 2
825 | NIRJ01 | IDMH103505 | DG | ID_PUNESOUTH | 458993 | NIRAWAGAJ | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS BER | New SMPS Required | Open | 2025-05-15 | 2.5 | 1.5 |  | 5 | 3
826 | NGP343 | IDMH109128 | DG | ID_NAGPUR | 531364 | NARSALA | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
827 | BHAN04 | IDMH100578 | DG | ID_CHANDRAPUR | 567156 | OPEN PLOT JAVAHARNAGAR | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
828 | PLSD01 | IDMH111466 | DG | ID_AMRAVATI | 458178 | PALASKHED | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 | 0.5 |  | 2
829 | HINJ63 | IDMH109769 | DG | ID_PUNESOUTH | 523348 | BHUMKAR WASTI WAKED | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-03-10 |  | 2.5 | 1.5 |  | 2
830 | HINJ12 | IDMH105248 | NON DG | ID_PUNESOUTH | 459032 | HINJEWADI CAPACITY (SYMBIOSIS) | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | BB | Low Battery Backup | BB replaced | Closed | 2025-03-31 |  | 1 | 1.5 |  | 2
831 | NGP118 | IDMH100655 | DG | ID_NAGPUR | 458386 | GANESH NAGAR | NAGPUR | SAI | MILIND RAMTEKE | RRU | RRU faulty | Support req | Open | VIL Support Required |  |  | 0.5 |  | 1
832 | NGPR73 | IDMH100657 | DG | ID_NAGPUR | 458364 | JUNI MANGALWARI | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
833 | AHRI01 | IDMH100681 | DG | ID_CHANDRAPUR | 460042 | AHERI | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
834 | ARNW01 | IDMH100682 | DG | ID_CHANDRAPUR | 458392 | AHERNAVARGAON | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 | 0.5 |  | 0.5 |  | 2
835 | PUN534 | IDMH106862 | NON DG | ID_PUNENORTH | 459308 | SYMBIOSIS KNOWLEDGE VILLAGE(RELOCATION) | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
836 | SLKS01 | IDMH100688 | DG | ID_CHANDRAPUR | 458221 | SALIKASA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
837 | NGP470 | INMH400919 | NON DG | ID_NAGPUR | 530179 | SURVE NAGAR | NAGPUR | SAI | KAILASH POKALE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 1 |  |  | 2 | 2
838 | HINJ40 | IDMH107732 | NON DG | ID_PUNESOUTH | 459022 | PERSISTANT | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
839 | PRNI01 | IDMH100482 | DG | ID_NAGPUR | 458124 | PARSHAWANI | NAGPUR | SAI | KAILASH POKALE | RRU | RRU Faulty | RRU replaced | Closed | 2025-02-28 |  | 1 |  |  | 1
840 | COOP01 | IDMH100733 | DG | ID_CHANDRAPUR | 451505 | CHOP_V_USO | NAGPUR | SAI | BEERENDRA SINGH | SMPS | RM Faulty | RM replaced | Closed | 2025-03-31 | 0.5 |  | 1.5 |  | 2
841 | HINJ34 | IDMH110555 | DG | ID_PUNESOUTH | 525626 | WIPRO TECHNOLOGIES,PHASE 2 | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Load Segregation | RRU at Critical | Load segregation done | Closed | 2025-04-09 | 7 | 2 | 5 | 2 | 4
842 | MLDI01 | IDMH103646 | DG | ID_PUNESOUTH | 458890 | MALWADI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan For Smps Rectification | Open | 2025-04-20 | 1.5 | 2 | 0.5 | 1 | 4
843 | KIBV01 | IDMH100749 | DG | ID_CHANDRAPUR | 458134 | KOCHI BARVA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
844 | PU1104 | IDMH109110 | NON DG | ID_PUNENORTH | 576787 | WALHEKARWADI 3 | PUNE-3 | ATS | Vacant CE Pune-3 | Load Segregation | RRU at Critical | RRU shifted to non critical | Closed | 2025-01-30 | 1.5 |  |  |  | 1
845 | GHUS06 | IDMH110056 | DG | ID_CHANDRAPUR | 523359 | MAIN BASTI-GUGGHUS | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 1 |  | 1
846 | DWHD01 | IDMH100845 | DG | ID_CHANDRAPUR | 458162 | DEWHADI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU faulty | Support req | Open | VIL Support Required | 0.5 |  |  |  | 1
847 | AMGM01 | IDMH100846 | DG | ID_CHANDRAPUR | 451396 | AMGAON MAHAL | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 1 |  |  | 2
848 | TMBD01 | IDMH100849 | DG | ID_CHANDRAPUR | 451428 | PATHARI/ TAMBEGADI MENDHA | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Faulty | Planned for SMPS rectification | Open | 2025-05-15 |  | 1 | 1.5 | 2 | 3
849 | SNDW01 | IDMH100852 | DG | ID_CHANDRAPUR | 458419 | SINDEWAHI | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
850 | RHPT01 | IDMH100870 | DG | ID_CHANDRAPUR | 451335 | ROHAPATMAREGAON | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
851 | LATR77 | INMH405753 | NON DG | ID_SOLAPUR | 592141 | Himayat Nagar | LATUR | PTPL | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 | 1.5 |  |  | 2
852 | AURN33 | IDMH103727 | DG | ID_AURANGABAD | 460374 | BAJAJ NAGAR | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | Smps Controller And Lvd Faulty | Rectification Pending | Open | 2025-04-20 | 0.5 | 1 |  |  | 2
853 | AKLE04 | INMH407201 | DG | ID_AHMEDNAGAR | 566500 | Â AKOLE MARKET | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | Low Battery Backup | BB replaced | Closed | 2025-04-24 | 1 | 0.5 |  | 1 | 3
854 | ARDP01 | IDMH100906 | DG | ID_NANDED | 460173 | ARDHAPUR | LATUR | PTPL | RAJKUMAR ALANE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 | 0.5 | 0.5 |  | 3
855 | TKBN01 | IDMH103520 | DG | ID_AHMEDNAGAR | 566404 | OPEN PLOT TAKLIBHAN | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | BB theft | New BB deployed | Closed | 2025-03-10 |  | 0.5 |  |  | 1
856 | SUUP01 | IDMH104676 | DG | ID_KOLHAPUR | 461289 | SUPE | KOLHAPUR | SSS | RITESH RANGOLE | RRU | RRU Faulty | Support req | Open | VIL Support Required |  |  | 0.5 | 2 | 2
857 | TKDJ01 | IDMH100920 | DG | ID_NAGPUR | 505307 | HINGANGHAT MIDC | NAGPUR | SAI | VIVEK GANJARE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
858 | PAJM39 | IDMH105006 | DG | ID_GOA | 461405 | BORIM | GOA | SSS | SUNIL TAMSE | BB | BB Backup 10 mIN | Plan for BB upgradation | Open | 2025-04-30 | 0.5 | 0.5 |  |  | 2
859 | PRNR01 | IDMH104183 | DG | ID_AHMEDNAGAR | 566849 | OPEN PLOT PARNER | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  | 0.5 | 5 | 3
860 | UMRN01 | IDMH103246 | DG | ID_NASHIK | 505243 | UMRANE | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 | 0.5 |  |  | 2
861 | PACH01 | IDMH111575 | DG | ID_AHMEDNAGAR | 464760 | PACHEGAON | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-10 | 0.5 | 1 |  |  | 2
862 | WAII07 | IDMH103630 | NON DG | ID_SATARA | 578725 | WAII MIDC_2 | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-05-22 |  | 1.5 |  |  | 1
863 | MNGN01 | IDMH105758 | DG | ID_RAIGARH | 458696 | MANGAON | PUNE-2 | ATS | AMAY DORUGADE | RRU | VIL RRU Faulty | RRU Replacement done | Closed | 2025-02-28 | 0.5 | 1 |  |  | 2
864 | KTLI01 | IDMH105729 | DG | ID_KOLHAPUR | 458394 | KOTHALI | KOLHAPUR | SSS | SANTOSH JADHAV | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 |  | 0.5 |  | 2
865 | TLWA01 | IDMH102540 | DG | ID_AURANGABAD | 460126 | TALWADA | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
866 | SNKD01 | IDMH101044 | DG | ID_NANDED | 459901 | SONKHED | LATUR | PTPL | Vacant CE Latur | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
867 | PGGN01 | IDMH103815 | DG | ID_AHMEDNAGAR | 505277 | POHEGAON | AHMEDNAGAR | PTPL | SANDEEP WANI | RRU | RRU faulty | RRU replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
868 | MGOA05 | IDMH106001 | DG | ID_RAIGARH | 458991 | TOLL BK | PUNE-2 | ATS | AMAY DORUGADE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
869 | NASK59 | IDMH103817 | NON DG | ID_NASHIK | 465640 | RELOCATION_NASK59 (NIRMALA CONVENT) | NASHIK | ATS | MANOJ SINHA | Load Segregation | RRU Was in Critical | RRU correction lone in Non critical | Closed | 2025-01-30 | 1 |  |  |  | 1
870 | WAHI01 | IDMH109020 | DG | ID_RAIGARH | 505446 | WADHAV | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 3 | 1
871 | ZOTR03 | INMH407569 | DG | ID_RAIGARH | 531747 | OPEN PLOT OF RAMCHANDRA PATIL | PUNE-3 | ATS | ANANT TIDKE | Cable | DCDB to RRU cable long distance 25m | cable distane reduction req | Open | VIL Support Required |  | 0.5 | 0.5 |  | 2
872 | MGOA06 | IDMH106165 | DG | ID_RAIGARH | 458997 | DASGAON | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS controller faulty | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
873 | FZPR01 | IDMH101076 | DG | ID_AKOLA | 458015 | FAIZPUR | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
874 | PAJ268 | IDMH105049 | DG | ID_GOA | 461433 | CUDDEGAL MINES_COW | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Controller fault | controller replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
875 | NGPR07 | IDMH101089 | DG | ID_NAGPUR | 458358 | PARSI ANJUMAN | NAGPUR | SAI | MILIND RAMTEKE | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
876 | SASI01 | IDMH101098 | DG | ID_CHANDRAPUR | 459827 | SASTI | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
877 | JATG01 | IDMH108602 | DG | ID_AHMEDNAGAR | 525440 | JATEGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-20 | 1 | 1 | 0.5 |  | 3
878 | DSBK01 | IDMH101109 | DG | ID_NANDED | 458676 | DIGRAS BUDRUK | LATUR | PTPL | RAJKUMAR ALANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
879 | MAHD04 | IDMH106839 | DG | ID_RAIGARH | 458988 | NADGAON TARF BIRWADI | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS Obsolute model | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
880 | LVNG01 | IDMH101131 | DG | ID_SOLAPUR | 459005 | LAVANGI | SOLAPUR | SAI | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
881 | CHTR01 | IDMH100994 | DG | ID_AMRAVATI | 451357 | CHATARI_V_USO | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 1 |  | 1 | 3 | 3
882 | YOLA02 | IDMH110744 | NON DG | ID_NASHIK | 465635 | RELOCATION_YOLA 02 | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-04-30 | 0.5 | 1 |  | 1 | 3
883 | YOLA10 | INMH406503 | NON DG | ID_NASHIK | 591773 | Airtel_Hudco Colony | NASHIK | ATS | Vacant Vacant CE Nashik | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-15 |  | 0.5 |  |  | 1
884 | NGON01 | IDMH107631 | DG | ID_RAIGARH | 458970 | NAGAON | PUNE-2 | ATS | AMAY DORUGADE | RRU | 1-RRU Malfunctiong | RRU rectification done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
885 | PUN269 | IDMH103933 | NON DG | ID_PUNENORTH | 458763 | AIAPPA TEMPLE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
886 | WRDH03 | IDMH101220 | NON DG | ID_NAGPUR | 458249 | KRISHNA NAGAR | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
887 | ADSU01 | IDMH100230 | DG | ID_AKOLA | 458001 | ADSUL | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
888 | BEED01 | IDMH101251 | DG | ID_AHMEDNAGAR | 460051 | BEED MARKET | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
889 | SWJE01 | IDMH100901 | DG | ID_AMRAVATI | 464897 | SAWARGAON JIRE | AKOLA | SAI | ALI SHAH | SMPS | SMPS BER | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
890 | SNBI01 | IDMH100930 | DG | ID_CHANDRAPUR | 505463 | SONBARDI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Delta SMPS BER | SMPS Replacement require | Open | 2025-05-30 | 0.5 |  |  |  | 1
891 | MLGA01 | IDMH103968 | DG | ID_KOLHAPUR | 459699 | MALGAON | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS Controller Faulty | SMPS Rectfication Req | Open | 2025-05-22 |  | 0.5 |  |  | 1
892 | SAVR01 | IDMH104005 | DG | ID_KOLHAPUR | 505481 | SAVARDE | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS Controller & LVD Faulty & BB Backup 10 Min | SMPS Rectfication & New BB Req | Open | 2025-04-30 |  | 0.5 |  |  | 1
893 | KADA01 | IDMH102059 | DG | ID_AHMEDNAGAR | 459337 | KADA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-07 | 0.5 | 0.5 | 0.5 |  | 3
894 | SANR04 | IDMH108846 | DG | ID_NAGPUR | 565747 | OPEN PLOT SAONER | NAGPUR | SAI | KAILASH POKALE | RRU | VIL RRU Faulty | RRU replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
895 | RIKD01 | IDMH101334 | NON DG | ID_AKOLA | 464877 | RUIKHEDE | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-04-09 |  |  | 1.5 | 1 | 2
896 | AKOT04 | IDMH101197 | DG | ID_AKOLA | 458063 | UJWAL NAGAR | AKOLA | SAI | Vacant CE Akola | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
897 | PLNR01 | IDMH102029 | DG | ID_AURANGABAD | 459869 | PIMPALNER | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS Faulty | SMPS Changed VIL RRU circtcal to Non circtcal loas changed done,all infra ok | Closed | 2025-01-30 | 0.5 |  |  |  | 1
898 | SADK01 | IDMH100743 | DG | ID_CHANDRAPUR | 458132 | SADAK ARJUNI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU shifting at site | NA | Closed | 2025-03-31 |  |  | 1 |  | 1
899 | NGPR41 | IDMH101410 | DG | ID_NAGPUR | 458237 | CHICHOLI (KHAPERKHEDA) | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
900 | SYTK01 | IDMH100902 | DG | ID_CHANDRAPUR | 451436 | SAYAT KHARADA | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 1 | 1 | 2
901 | LMPR01 | IDMH104084 | DG | ID_NASHIK | 458092 | LAKHAMAPUR | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
902 | STDH01 | IDMH101453 | DG | ID_SOLAPUR | 458925 | SHIRUR TAJBAND | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
903 | BIBI01 | IDMH102693 | DG | ID_AKOLA | 460027 | BIBI | AKOLA | SAI | RANJEET KAPSE | SMPS | smps controllar faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 |  | 0.5 |  | 2
904 | PU1005 | IDMH101469 | DG | ID_PUNESOUTH | 574610 | NICR | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 |  |  | 0.5 |  | 1
905 | LNTD01 | IDMH101321 | DG | ID_AMRAVATI | 464923 | LONI TAKDI | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS Backplane faulty Delta 4000 W | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
906 | AKLA49 | IDMH109939 | NON DG | ID_AKOLA | 565823 | RAMDASPETH NAGPUR | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS BER | Q1 SMPS Replacement planned | Open | 2025-04-30 | 1 |  |  | 3 | 2
907 | MLWA01 | IDMH106733 | DG | ID_AMRAVATI | 460093 | MULAWA | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS BER | Plan for smps rectification | Open | 2025-05-22 | 1 |  |  | 2 | 2
908 | SHGV01 | IDMH104145 | DG | ID_AHMEDNAGAR | 505470 | SHINGAVE | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-04-30 | 1 |  |  |  | 1
909 | CHBR01 | IDMH109985 | DG | ID_AMRAVATI | 565852 | CHANDURBAZAR | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-20 | 1 |  | 0.5 |  | 2
910 | BHAN14 | IDMH108196 | DG | ID_CHANDRAPUR | 567161 | MHADA COLONY (NR RAILWAY STATION BHANDRA) | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | Blvd Faulty | Plan for rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
911 | SURG01 | IDMH102641 | DG | ID_AHMEDNAGAR | 505278 | SUREGAON | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | BB Theft | BB install | Closed | 2025-05-30 | 0.5 |  |  |  | 1
912 | CHKN32 | IDMH104191 | DG | ID_PUNENORTH | 502992 | MOSHI TOLL NAKA | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 1 | 1.5 |  | 3
913 | YAVT02 | IDMH107809 | DG | ID_AMRAVATI | 565315 | REVATHI PRIDE-YAWATMAL | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
914 | WRJN01 | IDMH108106 | DG | ID_AMRAVATI | 524047 | WARA JAHANGIR | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
915 | UKPN01 | IDMH108474 | DG | ID_AMRAVATI | 523865 | UKALIPEN | AKOLA | SAI | ALI SHAH | SMPS | RM Faulty | RM Replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
916 | DGRS03 | IDMH108565 | DG | ID_AMRAVATI | 565845 | DIGRAS-2 | AKOLA | SAI | DHANRAJ NIBALKAR | RRU | RRU Faulty | Support req | Open | VIL Support Required |  |  | 1 |  | 1
917 | WDJI01 | IDMH108865 | DG | ID_AKOLA | 523923 | WADJI | AKOLA | SAI | RANJEET KAPSE | SMPS | controller faulty | controller to be replace | Open | 2025-04-30 |  |  | 0.5 |  | 1
918 | NGAL12 | IDMH109072 | DG | ID_AMRAVATI | 565314 | TIVSA | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 |  | 3.5 | 8 | 3
919 | BORA01 | IDMH101622 | DG | ID_SOLAPUR | 459687 | BORAMANI | SOLAPUR | SAI | BALASAHEB KADAM | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
920 | KHON01 | IDMH101627 | DG | ID_NANDED | 505315 | ALEGAON ( REPEATER OF KODRI ) | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-03-31 |  | 1 |  |  | 1
921 | TKLV01 | IDMH110295 | DG | ID_AKOLA | 465468 | TAKALI VIRO | AKOLA | SAI | RANJEET KAPSE | SMPS | controller faulty | controller to be replace | Open | 2025-04-30 |  |  | 0.5 | 1 | 2
922 | SAWA02 | INMH408550 | NON DG | ID_NAGPUR | 451467 | HALDIRAM_VF | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 1 | 2
923 | PU1540 | IDMH105381 | DG | ID_PUNESOUTH | 565887 | TUKAINGR | PUNE-1 | ATS | VIJAY KOLI | SMPS | Eltek power plant faulty | Automation done & Eltek complaint raised | Reopen | 2025-03-31 | 1 |  | 3.5 | 2 | 3
924 | PUNE08 | IDMH104242 | DG | ID_PUNESOUTH | 459225 | POONAM HEIGHTS | PUNE-2 | ATS | RAHUL TUPARE | SMPS | Smps Lvd Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
925 | LOHN01 | IDMH103537 | DG | ID_AHMEDNAGAR | 460104 | LOHGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Zero | Plan for BB upgradation | Open | 2025-05-30 | 1.5 |  |  |  | 1
926 | NGP469 | INMH402302 | NON DG | ID_NAGPUR | 571604 | GANESH PETH | NAGPUR | SAI | MILIND RAMTEKE | BB | BB Backup Very Low | New BB Installed | Closed | 2025-04-09 |  |  | 0.5 | 3 | 2
927 | JLGN06 | IDMH104266 | DG | ID_AKOLA | 566314 | OPEN PLOT PIMPRALA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 | 2 | 2
928 | DLGN01 | IDMH101610 | DG | ID_AKOLA | 464930 | DEULGAONRAJA | AKOLA | SAI | RANJEET KAPSE | BB | BB cell faulty | Plan for BB cell replacement | Open | 2025-05-15 | 0.5 |  | 0.5 | 1 | 3
929 | RGDH01 | IDMH103577 | DG | ID_AHMEDNAGAR | 460005 | RANJANGAON DESHMUKH | AHMEDNAGAR | PTPL | SANDEEP WANI | RRU | RRU faulty | RRU replaced | Closed | 2025-03-31 | 1 |  |  |  | 1
930 | SOL118 | INMH400443 | DG | ID_SOLAPUR | 565614 | TULJAPUR WES | SOLAPUR | PTPL | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
931 | DNGI01 | IDMH103605 | DG | ID_AHMEDNAGAR | 460058 | DHANGARWADI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | BB Backup low | BB upgradation done | Closed | 2025-05-30 |  | 0.5 |  |  | 1
932 | NBAN01 | IDMH101787 | DG | ID_SOLAPUR | 459514 | NIDEBAN | LATUR | SAI | SUDHIR AGHE | BB | BB Backup Very Low | mew BB installed | Closed | 2025-03-10 |  | 0.5 |  |  | 1
933 | PUN285 | IDMH104300 | DG | ID_PUNENORTH | 458764 | MOSHI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
934 | VRSL01 | IDMH107794 | DG | ID_RAIGARH | 458867 | VARSOLI | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-31 | 3.5 |  |  |  | 1
935 | PAJM59 | IDMH104308 | DG | ID_GOA | 461434 | CURTORIM | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Controller Faulty TT NO 240629CM2478866 | Plan for rectification | Open | 2025-04-30 |  |  | 1 | 1 | 2
936 | NAND21 | IDMH101846 | DG | ID_NANDED | 505338 | VISHNU NAGAR (VIP ROAD) | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 |  |  | 1
937 | SAGM03 | IDMH104323 | DG | ID_AHMEDNAGAR | 460270 | SANGAMNER MKT | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS BER | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
938 | KHUD01 | IDMH101882 | DG | ID_SATARA | 507077 | KHUDUS | SOLAPUR | PTPL | CHANDRAKANT ANGADI | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
939 | PUN809 | IDMH106588 | NON DG | ID_PUNESOUTH | 451287 | AXISBANK_VF | PUNE-2 | INHOUSE | AKSHAY SHELAR | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
940 | WANG01 | IDMH101953 | DG | ID_SATARA | 458835 | WANGI | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | SMPS LVD FAULTY | Rectification Pending | Open | 2025-05-22 | 0.5 |  |  |  | 1
941 | SAGM14 | IDMH107821 | DG | ID_AHMEDNAGAR | 524583 | AKOLE ROAD FILLIN_NEW | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB Backup low | BB replaced | Closed | 2025-04-24 | 0.5 |  |  |  | 1
942 | PU1547 | IDMH101927 | DG | ID_PUNESOUTH | 521184 | VEGA CENTRE | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
943 | PHUR01 | IDMH102024 | DG | ID_AKOLA | 458254 | PAHUR | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
944 | GNWD01 | IDMH104438 | DG | ID_SATARA | 458903 | GANESHWADI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS controller faulty | Plan for rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
945 | PUNE03 | IDMH105358 | DG | ID_PUNESOUTH | 459227 | SYNDICATE BANK | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
946 | NRGD01 | IDMH104451 | DG | ID_RAIGARH | 460057 | NIRGOODSAR | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | Smps Controller And Lvd Faulty | Rectification Pending | Open | 2025-05-07 | 1 | 4.5 | 1.5 | 2 | 4
947 | PUNE29 | IDMH105502 | NON DG | ID_PUNENORTH | 459241 | NAVLAKHA BLDG | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Faulty | RRU Replacement done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
948 | PRGT02 | IDMH105955 | DG | ID_PUNENORTH | 505201 | PIRANGUT | PUNE-2 | ATS | AKSHAY SHELAR | BB | Low Battery backup | BB replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
949 | PSHT01 | IDMH106523 | DG | ID_PUNESOUTH | 459560 | PANSHET | PUNE-2 | ATS | AKSHAY SHELAR | Cable | DCDB to RRU Underrated cable vtg drop 4.1v | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
950 | PUN817 | IDMH106565 | DG | ID_PUNESOUTH | 464785 | NDA ROAD_COW3 | PUNE-2 | ATS | AKSHAY SHELAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 2.5 |  |  |  | 1
951 | GNES01 | IDMH111626 | DG | ID_AHMEDNAGAR | 460010 | GANESHWADI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
952 | MRWD01 | IDMH106769 | DG | ID_PUNENORTH | 459417 | MARNEWADI | PUNE-2 | ATS | AKSHAY SHELAR | Cable | SMPS to RRU VLTG Drop >3v | cable to replace | Open | VIL Support Required | 1 | 2.5 |  |  | 2
953 | MDRP01 | IDMH102123 | DG | ID_SOLAPUR | 507057 | MANDRUP | SOLAPUR | PTPL | SATYASHIL PATIL | SMPS | MCB Faulty | MCB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
954 | AOLA01 | IDMH102132 | DG | ID_SATARA | 459295 | AKOLA | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
955 | PTRD05 | INMH005430 | NON DG | ID_AHMEDNAGAR | 565525 | PATHARDI, BHAGYASHRI BUILIDNG | AHMEDNAGAR | INHOUSE | DNYANESHWAR POTHARE | SMPS | SMPS controller faulty | Planned for SMPS rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
956 | AVNA01 | IDMH102165 | DG | ID_AURANGABAD | 458431 | AVHANA | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | BB | Low battery backup | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
957 | RULE01 | IDMH106837 | DG | ID_PUNESOUTH | 459619 | RULE | PUNE-2 | ATS | AKSHAY SHELAR | Cable | SMPS to RRU VLTG Drop >3v | cable to replace | Open | VIL Support Required | 0.5 |  |  |  | 1
958 | BOAN01 | IDMH100258 | DG | ID_NASHIK | 465741 | BORGAON | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
959 | AKLA05 | IDMH100558 | NON DG | ID_AKOLA | 583493 | Gajananpeth_New | AKOLA | SAI | Vacant CE Akola | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 1 |  |  | 1
960 | SOLP12 | IDMH102230 | DG | ID_SOLAPUR | 459774 | GURUNANAK NAGAR | SOLAPUR | SAI | SATYASHIL PATIL | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
961 | YAVT15 | IDMH100774 | DG | ID_AMRAVATI | 500184 | BANGAR NAGAR, YAVATMAL | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS Controller faulty | SMPS Replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
962 | PUN238 | IDMH107961 | DG | ID_PUNESOUTH | 459161 | PANDURANG COLONY | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
963 | UMLE01 | IDMH102289 | DG | ID_AKOLA | 457976 | UMALE | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required |  | 0.5 |  |  | 1
964 | WALS01 | IDMH102296 | DG | ID_SOLAPUR | 458840 | WALSANG | SOLAPUR | SAI | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
965 | PUN815 | IDMH108152 | DG | ID_PUNESOUTH | 459447 | NDA COW1_PUN815_COW | PUNE-2 | ATS | AKSHAY SHELAR | BB | Battery backup 30 min | Plan For new BB replacement | Open | 2025-05-30 |  |  | 0.5 |  | 1
966 | SEVL01 | IDMH102319 | DG | ID_AURANGABAD | 460400 | SEVALI | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  | 1 | 3
967 | KDAJ01 | IDMH104597 | DG | ID_PUNESOUTH | 458994 | KHANDAJ | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | Smps Controller Faulty | Controller replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
968 | PUN128 | IDMH105092 | DG | ID_PUNESOUTH | 459131 | HIRABAUG | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
969 | CHVT01 | IDMH109857 | NON DG | ID_PUNENORTH | 465347 | CHINMAYA VIBHOOTI AASHRAM | PUNE-2 | INHOUSE | AKSHAY SHELAR | Cable | DCDB to RRU Underrated cable vtg drop 3.3v | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
970 | PU1347 | IDMH110720 | DG | ID_PUNESOUTH | 507021 | BHUJABAL BAUG | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
971 | DRGN01 | IDMH102382 | DG | ID_AKOLA | 505098 | DHARANGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
972 | TELN01 | IDMH109944 | DG | ID_NAGPUR | 523868 | TELGAON | NAGPUR | SAI | KAILASH POKALE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 | 2.5 | 2 |  |  | 2
973 | MOHA01 | IDMH101021 | DG | ID_AMRAVATI | 460185 | MOHADI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS LVD Faulty | Plan for smps rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
974 | PLTR01 | IDMH103678 | DG | ID_AHMEDNAGAR | 460248 | PALASPUR | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS LVD Faulty | LVD Replaced | Closed | 2025-02-22 | 1.5 | 0.5 |  |  | 2
975 | NSBD01 | IDMH102412 | DG | ID_AKOLA | 565607 | OPEN PLOT, NASHIRABAD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 0.5 | 1 |  | 3 | 3
976 | JLGN22 | IDMH102425 | DG | ID_AKOLA | 565602 | JOSHI COLONY | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Low Battery Backup | BB upgradation done | Closed | 2025-03-31 | 1 | 0.5 |  |  | 2
977 | CKTN01 | IDMH102448 | DG | ID_SATARA | 458688 | CHIKALTHAN | SOLAPUR | SAI | BALASAHEB KADAM | Update pending | Update pending | Update pending | Update pending | Update pending | 1.5 | 0.5 |  |  | 2
978 | PUN278 | IDMH104306 | DG | ID_PUNESOUTH | 464800 | KATRAJGAON | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
979 | PUNE49 | IDMH112389 | DG | ID_PUNESOUTH | 459394 | RELOCATION OF HOTEL SAFARI BAVDHAN--PUNE49 (RELOCATION) | PUNE-2 | ATS | AKSHAY SHELAR | Cable | SMPS to RRU VLTG Drop >3v | cable to replace | Open | VIL Support Required | 2 |  | 0.5 |  | 2
980 | NBRE01 | IDMH102463 | DG | ID_AKOLA | 458016 | NIMBHORE | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
981 | PU1888 | INMH001142 | NON DG | ID_PUNESOUTH | 523490 | DHAYARI NR. GRAMPACHAYAT OFFICE | PUNE-2 | ATS | AKSHAY SHELAR | BB | Low Battery Backup | BB replaced | Closed | 2025-02-14 | 0.5 |  |  |  | 1
982 | NGP367 | IDMH109319 | DG | ID_NAGPUR | 521551 | GURUDEO NAGAR ALPHA_B | NAGPUR | SAI | MILIND RAMTEKE | RRU | RRU faulty | Support req | Open | VIL Support Required |  |  | 0.5 |  | 1
983 | PU1889 | INMH408558 | DG | ID_PUNESOUTH | 566495 | NAGAR_BIBWEWADI | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Faulty | RRU Replacement done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
984 | PU1959 | INMH407988 | DG | ID_PUNESOUTH | 451532 | SUTARHSPTL_VF | PUNE-2 | ATS | AKSHAY SHELAR | Cable | DCDB to RRU cable Voltage drop > 4 V | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
985 | NGP372 | IDMH112160 | DG | ID_NAGPUR | 565466 | DOBE NAGAR | NAGPUR | SAI | MILIND RAMTEKE | BB | BB Backup zero | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
986 | KHPA01 | IDMH101404 | DG | ID_NAGPUR | 458076 | KHAPA | NAGPUR | SAI | KAILASH POKALE | RRU | VIL RRU Faulty | RRU replaced | Closed | 2025-04-09 |  | 1.5 | 0.5 | 1 | 3
987 | NGP603 | INMH404294 | DG | ID_NAGPUR | 567108 | SURYA NAGAR / PARATWADA | NAGPUR | SAI | MILIND RAMTEKE | BB | BB Backup zero | Plan for BB upgradation | Open | 2025-05-15 | 1.5 | 0.5 |  | 1 | 3
988 | SANR09 | INMH405776 | NON DG | ID_NAGPUR | 591345 | Fincare Bank | NAGPUR | SAI | KAILASH POKALE | BB | Low Battery Backup | Plan for BB upgradation | Closed | 2025-03-31 | 0.5 |  | 0.5 |  | 2
989 | KLMN01 | IDMH102550 | DG | ID_SOLAPUR | 459468 | KALMAN | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | SMPS Controller fault | SMPS rectification done | Closed | 2025-01-30 | 1.5 |  |  |  | 1
990 | PNSK06 | IDMH105400 | DG | ID_NASHIK | 459973 | PATHARDI (NASHIK) | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
991 | TIGN01 | IDMH102560 | DG | ID_AHMEDNAGAR | 460281 | TISGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | RRU | RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 |  |  | 1
992 | RJAN02 | IDMH104767 | DG | ID_PUNENORTH | 459657 | RANJANGAON II | PUNE-1 | SAI | HARSHAL MAHAJAN | SMPS | SMPS Controller Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  | 1 | 2
993 | SWRG01 | IDMH102608 | DG | ID_SOLAPUR | 459477 | SAWARGAON | SOLAPUR | SAI | BALASAHEB KADAM | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
994 | MLGN18 | IDMH107381 | DG | ID_NASHIK | 507098 | DAYANA SHIVAR | NASHIK | ATS | SWAPNIL SALWE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 3.5 | 4.5 |  |  | 2
995 | DULE04 | IDMH110463 | DG | ID_NASHIK | 566386 | NEAR TO SHAH HOSPITAL,DHULE | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 2 | 2 | 2
996 | DULE23 | IDMH111913 | DG | ID_NASHIK | 505166 | STATION ROAD - DHULE | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
997 | DNGL01 | INMH003888 | DG | ID_NASHIK | 523888 | DONGRALE | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
998 | JEUR01 | IDMH103522 | DG | ID_SATARA | 458613 | JEUR | SOLAPUR | SAI | BALASAHEB KADAM | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
999 | STUR01 | IDMH102755 | DG | ID_SOLAPUR | 505335 | SASTUR | SOLAPUR | PTPL | ROHIT GHOLAP | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
1000 | LAKH01 | IDMH101437 | DG | ID_AMRAVATI | 458107 | LAKHPURI | AKOLA | SAI | Vacant CE Akola | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1001 | BRMT09 | IDMH104846 | DG | ID_PUNESOUTH | 458881 | BHIGWAN ROAD | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 1 | 0.5 | 1.5 | 4 | 4
1002 | DTHN01 | IDMH104858 | DG | ID_AHMEDNAGAR | 505251 | DEOTHAN | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS Backplane faulty | SMPS Rectification Done | Closed | 2025-02-11 |  | 0.5 |  |  | 1
1003 | PAJM91 | IDMH104873 | DG | ID_GOA | 461402 | BITS PILANI | GOA | SSS | SUNIL TAMSE | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
1004 | HTUR01 | IDMH102858 | DG | ID_SOLAPUR | 458847 | HATUR | SOLAPUR | SAI | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1005 | HGBK01 | IDMH102756 | DG | ID_SOLAPUR | 505320 | HARANGUL BK. | LATUR | PTPL | SUDHIR AGHE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1006 | MUDH01 | IDMH104888 | DG | ID_AURANGABAD | 460379 | MUDHALWADI | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | Load LVD Controller cable faulty | SMPS Replacement Required | Open | 2025-05-30 |  | 1 |  |  | 1
1007 | SOLP48 | IDMH101965 | DG | ID_SOLAPUR | 565773 | HATTURE NGR | SOLAPUR | PTPL | SATYASHIL PATIL | SMPS | LVD Faulty | LVD rectification done | Closed | 2025-03-07 | 0.5 |  | 0.5 |  | 2
1008 | BDLI01 | IDMH102785 | DG | ID_AKOLA | 458173 | BHADLI | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1009 | SOLP01 | IDMH102209 | DG | ID_SOLAPUR | 459780 | ASHRAYA LODGE | SOLAPUR | SAI | SATYASHIL PATIL | BB | BB Cell faulty | Plan for cell replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1010 | BGMP01 | IDMH103459 | DG | ID_SOLAPUR | 458843 | BEGAMPUR | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-02-28 | 1.5 | 0.5 |  |  | 2
1011 | NGP241 | IDMH107253 | DG | ID_NAGPUR | 520990 | HINGNA MIDC NILDOH | NAGPUR | SAI | KAILASH POKALE | RRU | RRU Faulty | RRU replaced | Closed | 2025-02-28 |  | 1 |  |  | 1
1012 | TSWD01 | IDMH102822 | DG | ID_AHMEDNAGAR | 459868 | TAMASWADI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | backpannel faulty | SMPS Rectification done | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1013 | PUNE32 | IDMH104331 | DG | ID_PUNESOUTH | 459172 | BUSINESS SQUARE, SADASHIV PETH | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1014 | KALM04 | INMH407341 | DG | ID_SOLAPUR | 505207 | KALAMB | SOLAPUR | PTPL | ROHIT GHOLAP | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required | 1 |  |  |  | 1
1015 | NGP358 | IDMH109992 | DG | ID_NAGPUR | 565413 | DINDAYAL NAGAR-1 | NAGPUR | SAI | KAILASH POKALE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1016 | TLWD01 | IDMH104161 | DG | ID_NASHIK | 458072 | TALWADE | NASHIK | ATS | SWAPNIL SALWE | Load Segregation | RRU was in Critical | RRU was correction Done Earlier,LVD Setting 44 to 45 Done | Closed | 2025-01-30 | 1 |  |  |  | 1
1017 | NGP249 | IDMH112001 | DG | ID_NAGPUR | 565397 | RAJENDRA NAGAR, NAGPUR | NAGPUR | SAI | KAILASH POKALE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-04-09 | 0.5 | 0.5 |  | 3 | 3
1018 | WIGL01 | IDMH101723 | DG | ID_AMRAVATI | 460396 | WAIGAUL | AKOLA | SAI | ALI SHAH | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  | 0.5 |  | 1 | 2
1019 | NGPR19 | IDMH100209 | DG | ID_NAGPUR | 458344 | SADAR (BAJAJ WINGS) | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  | 1 | 2
1020 | BLAJ02 | IDMH104964 | DG | ID_PUNESOUTH | 458697 | KAPURHOL (BALAJI) | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-02-28 |  | 2 |  |  | 1
1021 | HOLN01 | IDMH102965 | DG | ID_NASHIK | 458389 | HOLNANTHE | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-03-31 | 1 |  | 0.5 |  | 2
1022 | PSNR01 | IDMH102966 | DG | ID_NASHIK | 457983 | PALASNER | NASHIK | ATS | NILESH BHAVSAR | RRU | RRU faulty | RRU rectification req | Open | VIL Support Required | 1.5 |  |  |  | 1
1023 | ANGR34 | IDMH102974 | DG | ID_AHMEDNAGAR | 505506 | NAGAR FI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | operator LVD, rectifier communication | rectifcation done | Closed | 2025-04-30 | 0.5 |  |  |  | 1
1024 | RJNI01 | IDMH102979 | DG | ID_AURANGABAD | 460153 | RANJANI | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1025 | WRBK01 | IDMH103405 | DG | ID_AHMEDNAGAR | 460165 | WARURU BK | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1026 | PTHD01 | IDMH102998 | DG | ID_SOLAPUR | 459304 | PATHRUD | SOLAPUR | SAI | BALASAHEB KADAM | Cable | DCDB to RRU Drop > 3 V | VIL to Replace cable | Open | VIL Support Required |  | 1.5 |  |  | 1
1027 | NGP201 | IDMH107636 | DG | ID_NAGPUR | 500300 | HUDKESHWAR-3 | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1028 | GDCR01 | IDMH100241 | DG | ID_CHANDRAPUR | 460032 | GADCHANDUR | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1029 | NSK412 | INMH405730 | NON DG | ID_NASHIK | 589130 | Airtel_Rajiv Gandhi Nagar | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
1030 | RJAN03 | IDMH103046 | DG | ID_PUNENORTH | 459608 | RANJANGAON MIDC E-BLOCK | PUNE-1 | SAI | HARSHAL MAHAJAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1031 | KUKD01 | IDMH101736 | DG | ID_AMRAVATI | 458304 | KURANKHED | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1032 | MDNI01 | IDMH101824 | DG | ID_AMRAVATI | 451419 | MADANI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Controller Faulty | Plan for rectification | Open | 2025-05-22 |  |  | 1.5 | 1 | 2
1033 | NGAR01 | IDMH100035 | DG | ID_NAGPUR | 458138 | NAGARDHAN | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | LVD Setting Wrong | LVD setting done at 45 V DC | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1034 | KOLA01 | IDMH103072 | DG | ID_SATARA | 459376 | KOLA | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1035 | MARE01 | IDMH100595 | DG | ID_CHANDRAPUR | 460397 | MAREGAON | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS Controller Faulty | SMPS rectification done | Reopen | 2025-03-31 |  | 1.5 | 0.5 | 2 | 3
1036 | AMVT19 | IDMH101975 | DG | ID_AMRAVATI | 565307 | OPEN PLOT,WADALINAKA | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1037 | RJCY01 | IDMH100819 | DG | ID_CHANDRAPUR | 505284 | RAJUR | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1038 | SELU01 | IDMH103101 | DG | ID_NANDED | 459980 | SELU | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | BB | BB Backup Very Low | BB upgradation done | Closed | 2025-04-24 | 1 |  |  |  | 1
1039 | ANJN02 | IDMH102013 | DG | ID_AMRAVATI | 458022 | ANJANGAON | AKOLA | SAI | BHUSHAN BAREKAR | BB | BB Cell faulty | BB cell replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1040 | KPTE07 | IDMH108607 | DG | ID_NAGPUR | 567112 | KAMTEE-5 | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1041 | ARTE01 | IDMH103143 | DG | ID_NASHIK | 458096 | ARTHE | NASHIK | ATS | NILESH BHAVSAR | BB | BB cell open | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
1042 | PKHD01 | IDMH103144 | DG | ID_AURANGABAD | 458440 | PILKHOD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  | 0.5 | 0.5 |  | 2
1043 | BNDA01 | IDMH105230 | DG | ID_GOA | 461324 | BANDA | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-04-30 | 1.5 | 2 | 0.5 | 8 | 4
1044 | DNGD01 | IDMH102032 | DG | ID_AMRAVATI | 458140 | DHAMANGAON GADHI | AKOLA | SAI | BHUSHAN BAREKAR | BB | BB Cell faulty | Plan for cell replacement | Open | 2025-05-30 | 1 |  |  |  | 1
1045 | BALA01 | IDMH103176 | DG | ID_AURANGABAD | 458073 | BALAD BK. | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
1046 | KLSH01 | IDMH101461 | DG | ID_CHANDRAPUR | 460301 | KAILASH NAGAR | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 2 |  |  | 1 | 2
1047 | ANGR02 | IDMH103206 | DG | ID_AHMEDNAGAR | 460356 | GODAVARI COMPLEX | AHMEDNAGAR | PTPL | NILESH NAGDEVE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1048 | ASAL01 | IDMH102223 | DG | ID_AKOLA | 458247 | ASALGAON | AKOLA | SAI | RANJEET KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1049 | NGP104 | IDMH100201 | DG | ID_NAGPUR | 458334 | INDORA CHOWK | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1050 | GNRI01 | IDMH103592 | DG | ID_AURANGABAD | 460003 | GANORI | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | B L lvd & card controller C cable | Plan for rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1051 | VADL01 | IDMH105306 | DG | ID_NASHIK | 458058 | VADALI | NASHIK | ATS | NILESH BHAVSAR | Cable | EB Low voltage cause RM not functional & DCDB TO rru VOLTAGE DROP > 3 | EB Upgradation & VIL to replace Cable | Open | 2025-04-20 | 2 | 0.5 | 2 | 1 | 4
1052 | GOGN01 | IDMH100246 | DG | ID_CHANDRAPUR | 567188 | GOREGAON | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Load Segregation | BBU at Critical | BBU at non critical | Reopen | 2025-02-13 | 1.5 | 4 |  | 3 | 3
1053 | DGHT01 | IDMH102417 | DG | ID_AMRAVATI | 451510 | DAGADTHAR | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1054 | AUR137 | IDMH107030 | DG | ID_AURANGABAD | 531294 | BRIDGE WADI | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | SMPS Obsolute model/Single LVD PP | Plan for replacement | Open | 2025-04-30 | 1.5 | 0.5 |  |  | 2
1055 | SHRA05 | IDMH105334 | DG | ID_RAIGARH | 458858 | KALE | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS LVD Faulty | Complaint Raised to delta | Open | 2025-04-20 | 0.5 |  | 1 |  | 2
1056 | PCRA01 | IDMH103270 | DG | ID_AURANGABAD | 458317 | PACHORA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 0.5 | 1 | 0.5 | 1 | 4
1057 | JLGN78 | INMH404284 | DG | ID_AKOLA | 566331 | SHIRSOLI NAKA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Obsolute model/Single LVD PP | Plan for replacement | Open | 2025-04-30 | 0.5 |  |  |  | 1
1058 | LOTE02 | IDMH100531 | DG | ID_KOLHAPUR | 465800 | LOTE FILL IN | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-03-31 |  | 1 | 0.5 |  | 2
1059 | DDGN01 | IDMH103284 | DG | ID_AHMEDNAGAR | 460077 | DEDGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS Faulty | Plan for Rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
1060 | LNVL03 | IDMH105619 | DG | ID_RAIGARH | 459726 | KUSGAON BUDRUK | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS RM faulty | RM replaced | Closed | 2025-03-16 | 3 |  | 0.5 |  | 2
1061 | BRMT04 | IDMH105368 | DG | ID_PUNESOUTH | 464836 | BHAVANI NAGAR | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS BER | New SMPS Required | Open | 2025-05-30 |  | 2 |  | 2 | 2
1062 | JLGN12 | IDMH103295 | NON DG | ID_AKOLA | 458240 | RADHAKISHAN WADI | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | RM Faulty | RM replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1063 | WSHM07 | IDMH107222 | DG | ID_AMRAVATI | 566182 | RA COLLEGE | AKOLA | SAI | ALI SHAH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1064 | BLLR03 | IDMH101654 | DG | ID_CHANDRAPUR | 460329 | GANDHI CHOWK (BALLARSHAH) | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
1065 | LAKW01 | IDMH101877 | DG | ID_SATARA | 459419 | LAKHEWADI | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | LVD Faulty | SMPS rectification done | Closed | 2025-03-15 | 0.5 |  | 0.5 |  | 2
1066 | AGAR01 | IDMH103320 | DG | ID_SOLAPUR | 459478 | ANGAR | SOLAPUR | SAI | BALASAHEB KADAM | Cable | DCDB to RRU Drop > 3 V | VIL to Replace cable | Open | VIL Support Required | 1.5 |  |  |  | 1
1067 | WSHM08 | IDMH107416 | DG | ID_AMRAVATI | 531389 | HINGOLI ROAD | AKOLA | SAI | ALI SHAH | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1068 | LANI01 | IDMH102040 | DG | ID_AHMEDNAGAR | 460085 | LONI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | SMPS LVD Faulty | Plan for SMPS replacement | Open | 2025-05-15 | 1 | 1 |  |  | 2
1069 | BHAN02 | IDMH100798 | DG | ID_CHANDRAPUR | 458095 | MORE SUPER MKT, TUMSAR | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1070 | NAIN01 | IDMH101271 | DG | ID_SOLAPUR | 459451 | NAIGAON | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | LVD Faulty | Plan for rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1071 | GHWD01 | IDMH103370 | DG | ID_AHMEDNAGAR | 505489 | GADAKWADI(REPEATER MHAISGAON) | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-04-24 | 0.5 |  |  |  | 1
1072 | NCKU01 | IDMH101645 | DG | ID_SOLAPUR | 459421 | NAI CHAKUR | SOLAPUR | SAI | ROHIT GHOLAP | Cable | DCDB to RRU Underrated cable vtg drop 3.3v | Cable replacement req | Open | VIL Support Required |  | 1 |  |  | 1
1073 | UPLA01 | IDMH103384 | DG | ID_SOLAPUR | 505293 | UPALAI BK | SOLAPUR | PTPL | BALASAHEB KADAM | Cable | DCDB to RRU Drop > 3 V | VIL to Replace cable | Open | VIL Support Required | 0.5 | 0.5 | 0.5 |  | 3
1074 | FLMR01 | IDMH108480 | DG | ID_AMRAVATI | 523955 | FULUMARI | AKOLA | SAI | ALI SHAH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1075 | PBNI23 | IDMH108163 | NON DG | ID_NANDED | 531322 | ANAND NAGAR | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
1076 | AURN68 | IDMH103409 | NON DG | ID_AURANGABAD | 507090 | SOOT GIRNI CHOWK | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1077 | NAND65 | IDMH110732 | NON DG | ID_NANDED | 465485 | CHIKALWADI CORNER | LATUR | INHOUSE | Vacant CE Latur | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 |  | 1
1078 | NAND28 | IDMH102199 | NON DG | ID_NANDED | 460288 | SHIVAJI NAGAR | LATUR | PTPL | Vacant CE Latur | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 |  | 1
1079 | MTNG04 | INMH002258 | DG | ID_AKOLA | 505080 | MUKTAI NAGAR | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  | 1 | 2
1080 | ANUR01 | IDMH101702 | DG | ID_SOLAPUR | 459575 | ANDUR | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-16 | 0.5 |  | 0.5 |  | 2
1081 | NAND01 | IDMH101075 | DG | ID_NANDED | 460292 | OLD MONDA | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1082 | PUN580 | IDMH105467 | DG | ID_PUNENORTH | 573044 | KHARADI RESIDENTIAL | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-04-30 |  | 0.5 | 1.5 |  | 2
1083 | GNHP01 | IDMH108583 | DG | ID_AMRAVATI | 523984 | GANESHPUR_WASHIM | AKOLA | SAI | ALI SHAH | BB | Zero battery backup | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  | 1 | 2
1084 | SOLP25 | IDMH101907 | DG | ID_SOLAPUR | 459765 | KUMTENAKA | SOLAPUR | SAI | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1085 | SOLP33 | IDMH102208 | DG | ID_SOLAPUR | 459762 | VIJAY NAGAR | SOLAPUR | SAI | SATYASHIL PATIL | SMPS | LVD bypass | Plan for rectification SMPS | Open | 2025-05-22 |  | 0.5 |  |  | 1
1086 | NDAR01 | IDMH111702 | DG | ID_AURANGABAD | 464829 | NANDAR OF MR. SHIVAJI RAO SHABRAO KALE | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1087 | PCRA02 | IDMH103533 | DG | ID_AURANGABAD | 458316 | REST HOUSE RD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 1 |  | 1 |  | 2
1088 | YDRI01 | IDMH101769 | DG | ID_NANDED | 505270 | YELDARI | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Load Segregation | RRU at critical | RRU Shifted criticle to non criticle | Closed | 2025-03-10 | 1.5 | 0.5 |  |  | 2
1089 | MHTA01 | IDMH103556 | DG | ID_AHMEDNAGAR | 505469 | MOHATA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-15 | 1 | 0.5 |  |  | 2
1090 | GEGN01 | IDMH103404 | DG | ID_AURANGABAD | 458119 | GONDEGAON | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | LVD Card Faulty,Controller Faulty, RM back Panel faulty | LVD Card Faulty,Controller Faulty, RM back Panel faulty | Open | 2025-05-15 | 2 | 1.5 |  |  | 2
1091 | BHWL21 | IDMH109464 | DG | ID_AKOLA | 565751 | SINDHI COLONY | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required |  | 0.5 |  |  | 1
1092 | LASR01 | IDMH103541 | DG | ID_AURANGABAD | 460152 | LASUR | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | Smps Controller And Lvd Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 | 2.5 |  |  | 2
1093 | AMNR01 | IDMH103587 | NON DG | ID_AKOLA | 565298 | AMALNER | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 | 1 | 0.5 |  |  | 2
1094 | DABH01 | IDMH102309 | DG | ID_AURANGABAD | 460022 | DABHADI | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | BB | BB cell faulty | Plan for BB Cell Replacement | Open | 2025-04-30 | 1 | 1.5 |  |  | 2
1095 | CKWD01 | IDMH111675 | DG | ID_SATARA | 464853 | CHALKEWADI-SUZLON | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | Smps Controller Faulty | Controller to be replaced | Open | 2025-05-22 | 1.5 |  |  | 1 | 2
1096 | NGPR46 | IDMH100589 | DG | ID_NAGPUR | 458378 | VAISHALI NAGAR | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 | 1 | 2
1097 | CKGL01 | IDMH108837 | DG | ID_AMRAVATI | 523937 | CHIKHALGAD | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
1098 | SOYT01 | IDMH108850 | DG | ID_AMRAVATI | 523877 | SOYATA | AKOLA | SAI | ALI SHAH | BB | Low Batery backup | BB replaced | Closed | 2025-04-09 | 0.5 |  |  | 1 | 2
1099 | SELU05 | IDMH100638 | DG | ID_NANDED | 465810 | RAIGARH CORNER | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1100 | ASTI01 | IDMH103658 | DG | ID_AHMEDNAGAR | 459559 | ASTHI | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | LVD Byepass | Plan for rectification | Open | 2025-05-22 |  |  | 0.5 |  | 1
1101 | PTRD01 | IDMH103660 | DG | ID_AHMEDNAGAR | 460285 | PATHARDI | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1102 | ANGR16 | IDMH102705 | DG | ID_AHMEDNAGAR | 460350 | BURUDGAON | AHMEDNAGAR | PTPL | NILESH NAGDEVE | SMPS | BB Low Backup & SMPS BER | Replacement done | Closed | 2025-05-30 | 0.5 |  |  |  | 1
1103 | PAJM88 | IDMH106030 | DG | ID_GOA | 566764 | OPEN PLOT, COLVALE | GOA | SSS | SURAJ PATIL | SMPS | SMPS Faulty | Plan for SMPS replacement | Open | 2025-04-30 | 0.5 | 1 |  |  | 2
1104 | PUN231 | IDMH105625 | DG | ID_PUNESOUTH | 459068 | CENTREL STREET, CAMP | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1105 | PUN386 | IDMH106272 | DG | ID_PUNENORTH | 458751 | VALLABNAGAR | PUNE-3 | ATS | Vacant CE Pune-3 | Load Segregation | LVD Setting pending | Load shifted on non critical | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1106 | KARJ01 | IDMH102419 | DG | ID_SOLAPUR | 458822 | KARAJGAON | LATUR | SAI | SUDHIR AGHE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-20 |  | 1 | 0.5 |  | 2
1107 | SILA01 | IDMH102548 | DG | ID_SOLAPUR | 459416 | SHIRALA | LATUR | SAI | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1108 | JLGN57 | IDMH103720 | DG | ID_AKOLA | 566323 | ANURAG COLONY | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  | 0.5 | 1 |  | 2
1109 | SHDA01 | IDMH102883 | DG | ID_NASHIK | 457986 | SHAHADA | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-02-15 | 0.5 |  |  |  | 1
1110 | DULE01 | IDMH103734 | DG | ID_NASHIK | 457967 | PURTI BUILDING RELOCATION | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1111 | NGAL04 | IDMH100206 | DG | ID_NAGPUR | 458014 | KARANJA | NAGPUR | SAI | VIVEK GANJARE | SMPS | LLVD Card Faulty/Outdated PP | SMPS replaced | Closed | 2025-04-09 | 0.5 | 0.5 |  | 1 | 3
1112 | PUN428 | IDMH106492 | DG | ID_PUNENORTH | 458726 | DEHU ROAD (III) | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS Obsolute model | New SMPS Req | Open | 2025-04-30 |  | 1.5 | 1 |  | 2
1113 | ACHR01 | IDMH108911 | DG | ID_AKOLA | 523890 | ANCHARWADI | AKOLA | SAI | RANJEET KAPSE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
1114 | SAGM08 | IDMH103759 | DG | ID_AHMEDNAGAR | 460269 | GUNJALWADI | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1115 | RJKN01 | IDMH103768 | DG | ID_AURANGABAD | 458604 | RANJANGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan for SMPS replacement | Open | 2025-05-07 | 4 | 0.5 | 3.5 | 2 | 4
1116 | UMKH01 | IDMH103772 | DG | ID_AURANGABAD | 458437 | UMBARKHEDE | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1117 | RJTL01 | IDMH100997 | DG | ID_AURANGABAD | 460101 | RAJA TAKLI | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1118 | ADNR01 | IDMH103783 | DG | ID_AURANGABAD | 458418 | ANDHANER | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | BB | Low battery backup | Plan for BB upgradation | Open | 2025-04-30 | 1 | 2.5 |  |  | 2
1119 | JLJM02 | IDMH109905 | DG | ID_AKOLA | 565807 | JALGAON JAMOD-2 | AKOLA | SAI | RANJEET KAPSE | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 |  |  |  | 1
1120 | KNUR01 | IDMH104023 | DG | ID_AHMEDNAGAR | 505311 | KANHOOR | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS BLVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
1121 | DHGN01 | IDMH101889 | DG | ID_AHMEDNAGAR | 505269 | DAHIGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | BB replaced | Closed | 2025-04-09 | 0.5 | 1.5 |  | 1 | 3
1122 | BODI01 | IDMH101838 | DG | ID_AKOLA | 458020 | BORDI | AKOLA | SAI | Vacant CE Akola | SMPS | SMPS Delta 4000 W LVD faulty | SMPS Rectification require | Open | 2025-04-30 |  | 0.5 |  |  | 1
1123 | NAND03 | IDMH101085 | DG | ID_NANDED | 460290 | KALA MANDIR | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 |  |  | 1
1124 | TDKL01 | IDMH101194 | DG | ID_NANDED | 460344 | TADKALAS | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Load Segregation | Baseband critical | Baseband critical to non critical | Closed | 2025-03-31 | 0.5 | 0.5 |  |  | 2
1125 | BHDR01 | IDMH103060 | DG | ID_KOLHAPUR | 459651 | BAHADURWADI | KOLHAPUR | SSS | VINOD SAWANT | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1126 | PRND01 | IDMH103859 | DG | ID_SOLAPUR | 459746 | PARANDA | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | SMPS LVD & CONTROLLER FAULTY | New SMPS Installed | Closed | 2025-01-30 | 1 |  |  |  | 1
1127 | BEMB01 | IDMH103873 | DG | ID_SATARA | 459420 | BEMBALE | SOLAPUR | SAI | BALASAHEB KADAM | SMPS | SMPS LVD & CONTROLLER FAULTY | Rectification Pending | Open | 2025-05-22 | 1.5 |  |  |  | 1
1128 | KRDA01 | IDMH102995 | DG | ID_AHMEDNAGAR | 464828 | KHARDA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS Faulty | SMPS Replaced | Closed | 2025-01-08 | 0.5 |  |  |  | 1
1129 | PUN370 | IDMH105784 | NON DG | ID_PUNENORTH | 459125 | YERAWADA BAZAR | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  | 1 |  |  | 1
1130 | PPKD01 | IDMH102985 | DG | ID_NASHIK | 458427 | PIMPARKHED | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS RM Faulty due to vtg flutuation | Plan for Vtg rectification | Open | 2025-04-20 | 3.5 | 4 | 4 |  | 3
1131 | NAND07 | IDMH106933 | DG | ID_NANDED | 505077 | MUNDKHED | LATUR | PTPL | RAJKUMAR ALANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1132 | PJWL01 | IDMH104209 | DG | ID_AHMEDNAGAR | 460088 | JAWALA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | BB replaced | Closed | 2025-02-08 |  | 0.5 |  |  | 1
1133 | PRHL01 | IDMH103043 | DG | ID_NASHIK | 458430 | PIMPRI HAVELI | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
1134 | GHTW01 | IDMH105835 | DG | ID_AHMEDNAGAR | 459732 | GHOTAWI | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | Smps Lvd Faulty | Rectification Pending | Open | 2025-05-22 | 1 |  |  |  | 1
1135 | GDKR01 | IDMH101285 | DG | ID_NAGPUR | 464895 | GHONDKHERI | NAGPUR | SAI | KAILASH POKALE | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 1 | 1.5 |  | 2 | 3
1136 | HRTL01 | IDMH103365 | DG | ID_KOLHAPUR | 459822 | HATKANAGALE | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1137 | PUN382 | IDMH105845 | NON DG | ID_PUNENORTH | 459106 | P.D.C.C. SAHAKARI BANK | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS BER & BB Zero backup | New SMPS & BB Req | Open | 2025-04-30 | 1 | 1 | 1 | 2 | 4
1138 | KHAR01 | IDMH111428 | DG | ID_NAGPUR | 507113 | KHAIRGAON | NAGPUR | SAI | KAILASH POKALE | SMPS | Obsolute model/Single LVD SMPS | Q1 SMPS Replacement planned | Open | 2025-05-30 | 2.5 |  |  |  | 1
1139 | RTDR01 | IDMH103375 | DG | ID_KOLHAPUR | 505482 | RETHARE DHARAN | KOLHAPUR | SSS | VINOD SAWANT | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1140 | KRML01 | IDMH104008 | DG | ID_SOLAPUR | 459509 | KARMALA | SOLAPUR | SAI | BALASAHEB KADAM | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 1 |  | 2
1141 | ASVI01 | IDMH104027 | DG | ID_AHMEDNAGAR | 460336 | ASHWI BUDRUK | AHMEDNAGAR | PTPL | SANDEEP WANI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1142 | CHKS01 | IDMH103499 | DG | ID_KOLHAPUR | 505280 | KASBA CHIKLI | KOLHAPUR | SSS | RITESH RANGOLE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
1143 | PRLI05 | IDMH111503 | DG | ID_AHMEDNAGAR | 566150 | PARLI OLD CITY | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1144 | MOPD01 | IDMH105892 | DG | ID_NASHIK | 458457 | MOHAPADA | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 | 0.5 |  |  | 2
1145 | NAND39 | IDMH101323 | NON DG | ID_NANDED | 465893 | RELOCATION OF LANGAR GURUDWARA SAHIB (NAND39) | LATUR | INHOUSE | Vacant CE Latur | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
1146 | LOVY01 | IDMH104070 | DG | ID_AHMEDNAGAR | 458723 | LONI VYANKNATH | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1147 | RARI01 | IDMH104073 | DG | ID_AHMEDNAGAR | 458864 | RAJURI | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS LVD Faulty | Planned for SMPS rectification | Open | 2025-05-22 | 1 |  |  |  | 1
1148 | ARAI01 | IDMH103810 | DG | ID_NASHIK | 458051 | ARAI | NASHIK | ATS | Vacant Vacant CE Nashik | BB | Back Plaine ,RM & Controller Faulty,BB 2 Cell Faulty | SMPS Replaced & Rectification Done,LVD Setting 44 to 45 Done,BB 2 Cell Require | Open | 2025-05-30 |  | 0.5 |  |  | 1
1149 | PMRJ01 | IDMH104100 | DG | ID_AURANGABAD | 459891 | PIMPRI RAJA | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
1150 | KOLP10 | IDMH103854 | DG | ID_KOLHAPUR | 459809 | SAMBHAJINAGAR | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 1 |  |  | 1
1151 | PUN738 | IDMH106443 | NON DG | ID_PUNENORTH | 503293 | SECTOR 13 | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | SMPS old model BER | SMPS to chnaged | Open | 2025-05-15 | 1.5 |  | 0.5 |  | 2
1152 | KARD10 | IDMH104024 | DG | ID_SATARA | 459329 | SHANIWAR PETH | KOLHAPUR | SSS | VINOD SAWANT | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1153 | DGVE01 | IDMH104147 | DG | ID_NASHIK | 458024 | DIGHAVE | NASHIK | ATS | NILESH BHAVSAR | BB | BB connecting cable burnt | cable replaced | Closed | 2025-03-31 |  |  | 3 |  | 1
1154 | LNKD01 | IDMH104423 | DG | ID_NASHIK | 457979 | LONKHEDA | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-02-20 |  | 1.5 |  |  | 1
1155 | SIVD01 | IDMH104175 | DG | ID_NASHIK | 459885 | SHIVADE | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1156 | NGSL01 | IDMH104200 | DG | ID_NASHIK | 460393 | NAGARSUL | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1157 | AKLW01 | IDMH104113 | DG | ID_NASHIK | 457984 | AKKALKUWA | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-04-09 | 0.5 |  |  | 1 | 2
1158 | PNAB06 | IDMH104227 | DG | ID_AHMEDNAGAR | 460357 | AHMEDNAGAR MIDC | AHMEDNAGAR | PTPL | NILESH NAGDEVE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1159 | MUDL01 | IDMH104141 | DG | ID_KOLHAPUR | 458965 | MUDAL | KOLHAPUR | SSS | RITESH RANGOLE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
1160 | NGPR14 | IDMH100527 | DG | ID_NAGPUR | 458323 | KAMPTEE | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1161 | THSL01 | IDMH106007 | DG | ID_KOLHAPUR | 458705 | THASALWADI | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | Smps Controller And Lvd Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1162 | NARL01 | IDMH111447 | DG | ID_AMRAVATI | 451539 | NINGNUR GAHAGIR / NARALI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | smps controllar faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1163 | KDRI01 | IDMH102036 | DG | ID_AKOLA | 458174 | KANDARI | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1164 | PUN228 | IDMH106685 | DG | ID_PUNENORTH | 458747 | PIMPRI MIDC | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1165 | CKDR02 | IDMH112319 | DG | ID_AMRAVATI | 565357 | CHIKHALDARA | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
1166 | BLDN12 | IDMH112351 | DG | ID_AKOLA | 565641 | RAM NAGAR | AKOLA | SAI | RANJEET KAPSE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 1 |  |  | 1
1167 | PU1024 | IDMH107136 | DG | ID_PUNENORTH | 574929 | LAXMI NAGAR | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 3 |  | 1 | 2
1168 | BRHM01 | IDMH104302 | DG | ID_AHMEDNAGAR | 459334 | BRAHMANGAON | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | SMPS RECTIFICATION DONE | Closed | 2025-01-19 | 0.5 |  |  |  | 1
1169 | RANG01 | IDMH104303 | DG | ID_KOLHAPUR | 505292 | RANGOLI | KOLHAPUR | SSS | SANTOSH JADHAV | VIL Planned Activity | L900work done | NA | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1170 | DGLR01 | IDMH101625 | DG | ID_NANDED | 459303 | DEGLUR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Controller Faulty | SMPS rectification done | Closed | 2025-04-24 | 1 |  | 0.5 |  | 2
1171 | PDKV04 | INMH400417 | DG | ID_CHANDRAPUR | 500187 | PANDHARKAWDA 3 | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1172 | ALBG03 | IDMH107353 | DG | ID_RAIGARH | 570321 | ALIBAUG | PUNE-3 | ATS | ANANT TIDKE | Cable | DCDB to RRU cable long distance 30m | cable distane reduction req | Open | VIL Support Required |  | 0.5 |  |  | 1
1173 | KOLP57 | IDMH104345 | DG | ID_KOLHAPUR | 565916 | HOCKEY STADIUM | KOLHAPUR | SSS | SANTOSH JADHAV | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1174 | GARG01 | IDMH104349 | DG | ID_AHMEDNAGAR | 459668 | GHARGAON | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1175 | DHWD01 | IDMH104363 | DG | ID_AKOLA | 458105 | DAHIWAD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | Cantroller Faulty | Plan for rectification | Open | 2025-05-22 |  |  | 0.5 |  | 1
1176 | PMPL01 | IDMH104445 | DG | ID_NASHIK | 460293 | PIMPALGAON BASWANT | NASHIK | ATS | Vacant Vacant CE Nashik | Cable | DCDB to RRU voltage >4V underrated Al cable | cable replacement required | Open | VIL Support Required | 2.5 |  |  |  | 1
1177 | PUN322 | IDMH104377 | NON DG | ID_PUNESOUTH | 459176 | BHAVANI PETH | PUNE-2 | INHOUSE | RAHUL TUPARE | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1178 | SKRI01 | IDMH103316 | DG | ID_NASHIK | 458266 | SAKRI | NASHIK | ATS | NILESH BHAVSAR | SMPS | LVD Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  |  | 1 | 2
1179 | MSHT01 | IDMH104404 | DG | ID_AHMEDNAGAR | 460325 | MURSHATPUR | AHMEDNAGAR | PTPL | SANDEEP WANI | RRU | RRU faulty | RRU replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1180 | BSSE01 | IDMH104407 | DG | ID_SATARA | 459323 | BHOSE (MANGALVEDHA) | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Back panal faulty | Plan for SMPS rectification | Open | 2025-05-07 | 0.5 | 0.5 | 1 |  | 3
1181 | PPLG01 | IDMH100009 | DG | ID_CHANDRAPUR | 458144 | PIMPALGAON (SADAK) | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1182 | MLBK01 | IDMH104415 | DG | ID_AHMEDNAGAR | 464832 | MALUNJE BK | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB cell faulty | Plan for BB Cell Replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
1183 | KOLP14 | IDMH104487 | DG | ID_KOLHAPUR | 459821 | KASBA BAWDA | KOLHAPUR | SSS | RITESH RANGOLE | BB | BB 6 cell faulty/Backup 15min | BB Cell to be replace | Open | 2025-05-30 | 0.5 |  |  |  | 1
1184 | CMTN01 | IDMH104470 | DG | ID_NASHIK | 457990 | CHIMTHANA | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-15 | 0.5 |  |  |  | 1
1185 | SRKD01 | IDMH105514 | DG | ID_NASHIK | 458033 | SARANGKHEDA | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-04-24 | 1 | 1 |  |  | 2
1186 | AKLR01 | IDMH104495 | DG | ID_AHMEDNAGAR | 460055 | AKOLNER | AHMEDNAGAR | PTPL | NILESH NAGDEVE | BB | BB cell faulty | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
1187 | PAUD01 | IDMH106255 | DG | ID_PUNESOUTH | 459353 | PAUD | PUNE-2 | ATS | AKSHAY SHELAR | Cable | Underrated Cable | Cable replacement req | Open | VIL Support Required | 0.5 |  |  | 2 | 2
1188 | MUGT01 | IDMH102098 | DG | ID_NANDED | 460342 | MUGHAT | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-04-24 | 2.5 | 2 | 2 | 3 | 4
1189 | PUN348 | IDMH107397 | DG | ID_PUNENORTH | 458754 | SAMBAJINAGAR | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1190 | JLGN11 | IDMH104540 | DG | ID_AKOLA | 507038 | JAIN IRRIGATION (H/W) | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Faulty | SMPS rectification done | Closed | 2025-03-31 | 1.5 | 2 | 1 |  | 3
1191 | PAJ163 | IDMH106293 | NON DG | ID_GOA | 461435 | ARLEM | GOA | SSS | SUNIL TAMSE | SMPS | SMPS LVD faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  |  |  | 1
1192 | SHGN08 | INMH407422 | DG | ID_AKOLA | 531508 | ANAND SAGAR | AKOLA | SAI | RANJEET KAPSE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 | 0.5 |  | 2
1193 | NASK14 | IDMH106326 | DG | ID_NASHIK | 459966 | PANCHAVATI | NASHIK | ATS | MANOJ SINHA | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1194 | KLBM01 | IDMH106336 | DG | ID_RAIGARH | 570318 | WARE KALAMB | PUNE-3 | ATS | ANANT TIDKE | Cable | DCDB to RRU cable long distance 22m | cable distane reduction req | Open | VIL Support Required | 1 | 1 |  |  | 2
1195 | MALE04 | INMH406840 | NON DG | ID_AMRAVATI | 565819 | MALEGAON 3 | AKOLA | SAI | ALI SHAH | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-15 | 1 | 1 |  |  | 2
1196 | PRDA05 | INMH405767 | NON DG | ID_AMRAVATI | 592974 | Narayanpur_Airtel | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Eltek SMPS 4000 W LVD faulty | SMPS Rectification require | Open | 2025-04-20 | 4 | 0.5 | 1 |  | 3
1197 | PUNE98 | IDMH104643 | NON DG | ID_PUNESOUTH | 459201 | RASTA PETH | PUNE-2 | ATS | RAHUL TUPARE | BB | BB Backup very low | BB replaced | Closed | 2025-02-28 |  | 1 |  |  | 1
1198 | PU1522 | IDMH104649 | DG | ID_PUNENORTH | 570458 | MAHESH NAGER _PIMPRI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1199 | NGPR51 | IDMH100318 | DG | ID_NAGPUR | 458376 | SEMINARY HILL | NAGPUR | SAI | LEELADHAR BHOSKAR | SMPS | Emerson Single LVD absolute model | Need New SMPS | Open | 2025-05-30 | 1 |  |  | 2 | 2
1200 | MLPR02 | IDMH104860 | DG | ID_KOLHAPUR | 505291 | SHAHUWADI | KOLHAPUR | SSS | SANTOSH JADHAV | RRU | RRU Faulty | Support req | Open | VIL Support Required | 0.5 | 0.5 | 1.5 | 2 | 4
1201 | KTND01 | IDMH102222 | DG | ID_NANDED | 459336 | KARAM TANDA | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1202 | PUN356 | IDMH106424 | DG | ID_PUNENORTH | 458740 | MORYA GOSAVI MANDIR | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1203 | PUNE78 | IDMH106480 | DG | ID_PUNESOUTH | 464758 | BHUSARI CLNY | PUNE-2 | ATS | AKSHAY SHELAR | Cable | DCDB to RRU cable Voltage drop > 4 V | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1204 | PUN853 | IDMH106504 | DG | ID_PUNENORTH | 522089 | NEAR TREASURE PARK | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1205 | DGRS01 | IDMH101254 | DG | ID_AMRAVATI | 460399 | DIGRAS | AKOLA | SAI | DHANRAJ NIBALKAR | Cable | SMPS to DCDB Underated cable & Voltage drop > 3 V | cable to replace | Open | 2025-04-20 |  | 0.5 |  |  | 1
1206 | CHPD03 | IDMH102276 | DG | ID_AKOLA | 458260 | CHPD03 RELOCATION | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 | 1.5 |  | 1.5 |  | 2
1207 | BMBD01 | IDMH105282 | DG | ID_KOLHAPUR | 505267 | BHAMVAWADE | KOLHAPUR | SSS | SANTOSH JADHAV | VIL Planned Activity | L900work done | NA | Closed | 2025-03-31 | 1 |  |  |  | 1
1208 | HINJ20 | IDMH105401 | NON DG | ID_PUNESOUTH | 458985 | WIPRO PHASE 3 | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1209 | PU1166 | IDMH110140 | NON DG | ID_PUNENORTH | 528490 | INCOME TAX COLONY_NEW | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  | 0.5 | 1 | 3
1210 | ERND01 | IDMH104890 | DG | ID_AKOLA | 457970 | ERANDOL | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 6 | 1
1211 | KRJU01 | IDMH104895 | DG | ID_AHMEDNAGAR | 460284 | KARJULE HARYA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 1 |  | 0.5 |  | 2
1212 | BBRI01 | IDMH101354 | DG | ID_CHANDRAPUR | 505456 | BORI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Controller faulty | Rectification required | Open | 2025-05-22 | 0.5 |  |  |  | 1
1213 | MNTH01 | IDMH102509 | DG | ID_NANDED | 460014 | MANATHA | LATUR | PTPL | RAJKUMAR ALANE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 2 | 0.5 |  |  | 2
1214 | LNVL02 | IDMH106581 | DG | ID_RAIGARH | 459662 | TUNGRALI | PUNE-3 | ATS | PRATIK HULAVALE | RRU | RRU Faulty | RRU rectification done | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1215 | PUN986 | IDMH107940 | DG | ID_PUNENORTH | 566832 | BHOSARI | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 | 2 |  | 2
1216 | MNRD01 | IDMH102297 | DG | ID_NANDED | 505114 | MANWAT RD | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required | 0.5 |  |  |  | 1
1217 | LBGN01 | IDMH101525 | DG | ID_NANDED | 460319 | LIMBGAON | LATUR | PTPL | Vacant CE Latur | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
1218 | PAJM10 | IDMH105703 | DG | ID_GOA | 461446 | FARNANDES LAND | GOA | SSS | SUNIL TAMSE | BB | Low battery backup | Need to replace BB | Open | 2025-04-30 | 0.5 |  |  |  | 1
1219 | PUN169 | IDMH106610 | NON DG | ID_PUNENORTH | 458796 | CHINCHWADGAON | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 0.5 | 0.5 | 1 | 4
1220 | BHLD01 | IDMH102330 | DG | ID_AKOLA | 458023 | BHALOD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Obsolute model/Single LVD PP | New SMPS Req | Open | 2025-05-30 | 1 |  |  |  | 1
1221 | PUN721 | IDMH104965 | NON DG | ID_PUNENORTH | 464863 | HOTEL IBIS(OUTDOOR + IBS) | PUNE-1 | INHOUSE | VIJAY KOLI | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 |  |  | 0.5 | 1 | 2
1222 | NGPR82 | IDMH101836 | DG | ID_NAGPUR | 458131 | NARSALA | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS RM Faulty | RM replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1223 | WRNA02 | IDMH103750 | DG | ID_KOLHAPUR | 459697 | WARNA KODOLI | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1224 | NKBH02 | IDMH105010 | DG | ID_NASHIK | 460095 | IGATPURI | NASHIK | ATS | SUBHASH SHINDE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required |  | 0.5 |  |  | 1
1225 | SELU02 | IDMH102358 | DG | ID_NANDED | 505504 | VIVEKANAND NAGAR-SELU | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | SMPS | SMPS BER | New SMPS Require | Open | 2025-05-15 | 1 | 1.5 |  |  | 2
1226 | LATR37 | IDMH111070 | DG | ID_SOLAPUR | 566147 | SONA NAGAR | LATUR | PTPL | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1227 | WKAD01 | IDMH102052 | DG | ID_AMRAVATI | 460002 | WAKAD | AKOLA | SAI | ALI SHAH | SMPS | SMPS Delta 4000 W Controller faulty and BER Single LVD Provision/Emerson 3200 W SMPS BER | SMPS replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1228 | CKLA01 | IDMH102798 | DG | ID_AKOLA | 505490 | CHIKHALA | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS BER | New SMPS Req | Open | 2025-05-07 | 2 | 2.5 | 1.5 | 1 | 4
1229 | MAHA01 | IDMH102631 | DG | ID_AMRAVATI | 566214 | MAHAGAON | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS Delta 4000 W LVD card faulty | SMPS rectification done | Closed | 2025-03-14 | 2.5 |  | 0.5 |  | 2
1230 | DOGR01 | IDMH106706 | DG | ID_NASHIK | 458426 | DEOGHAR(CHILLARPADA) | NASHIK | ATS | MANOJ SINHA | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 |  |  | 0.5 |  | 1
1231 | BNOD01 | IDMH102422 | DG | ID_AKOLA | 458037 | BAMNOD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-04-09 | 2 |  | 0.5 | 1 | 3
1232 | VISP01 | IDMH105056 | DG | ID_AHMEDNAGAR | 459501 | VISAPUR | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS BER | Planned for SMPS replacement | Open | 2025-04-30 |  | 0.5 |  |  | 1
1233 | RHGD01 | IDMH102473 | DG | ID_AURANGABAD | 460074 | ROHILAGAD | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1234 | THBD01 | IDMH105067 | DG | ID_NASHIK | 458177 | TAHARABAD | NASHIK | ATS | Vacant Vacant CE Nashik | BB | BB cell faulty | Plan for cell replacement | Open | 2025-05-30 | 1 |  |  |  | 1
1235 | PUN195 | IDMH105114 | DG | ID_PUNENORTH | 458748 | INDRAYANI NAGAR III | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | SMPS BER | SMPS replaced | Closed | 2025-04-24 | 1 |  | 0.5 |  | 2
1236 | TURL01 | IDMH106490 | DG | ID_KOLHAPUR | 459382 | TURAL | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | controller faulty/LVD bypassed | SMPS rectification planned | Open | 2025-05-22 | 0.5 |  |  |  | 1
1237 | ICKJ25 | IDMH112191 | DG | ID_KOLHAPUR | 566858 | STATION ROAD,ICHALKARANJI | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1238 | AURN64 | IDMH102512 | NON DG | ID_AURANGABAD | 460207 | PARIJAT NAGAR | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1239 | TLGN07 | IDMH105143 | NON DG | ID_RAIGARH | 458671 | THAKUR CENTER | PUNE-3 | ATS | PRATIK HULAVALE | RRU | VIL RRU Faulty | RRU Replacement done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1240 | PUN114 | IDMH105146 | DG | ID_PUNESOUTH | 464889 | BANER | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1241 | RATN01 | IDMH106169 | DG | ID_KOLHAPUR | 459593 | RATNAGIRI | KOLHAPUR | SSS | VIVEK GOSAVI | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 1 |  |  | 2
1242 | LMPT01 | IDMH105169 | DG | ID_NASHIK | 458421 | LAKHMAPUR PHATA | NASHIK | ATS | Vacant Vacant CE Nashik | RRU | RRU faulty | Support req | Open | VIL Support Required | 1 |  |  |  | 1
1243 | PUNE27 | IDMH105198 | DG | ID_PUNESOUTH | 464885 | SHIVALAYA, AUNDH | PUNE-2 | ATS | VIPIN GUPTA | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 1 |  |  | 1
1244 | YAVT09 | IDMH100272 | NON DG | ID_AMRAVATI | 458399 | RAYMONDS | AKOLA | INHOUSE | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
1245 | SNGM02 | IDMH106797 | DG | ID_KOLHAPUR | 459484 | SANGAMESHWAR HILL | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 1 |  |  | 2
1246 | PAJM40 | IDMH103997 | NON DG | ID_GOA | 461440 | BENAULIM | GOA | SSS | SUNIL TAMSE | SMPS | SMPS Controller faulty | Complaint Lodge for SMPS Controller | Open | 2025-04-30 | 0.5 |  |  |  | 1
1247 | LVHL01 | IDMH107955 | DG | ID_AKOLA | 565798 | LAVANA REPEATER | AKOLA | SAI | RANJEET KAPSE | SMPS | Controller faulty | Q1 SMPS Replacement planned | Open | 2025-05-30 | 0.5 |  |  |  | 1
1248 | CHKN08 | IDMH105292 | DG | ID_PUNENORTH | 459663 | CHAKAN MARKET | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB Backup very low | BB replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1249 | JLGN01 | IDMH102835 | DG | ID_AKOLA | 458246 | SWATANTRA CHOWK | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 | 1 | 2
1250 | NASK77 | IDMH104240 | DG | ID_NASHIK | 459907 | AURANGABAD BYPASS | NASHIK | ATS | MANOJ SINHA | SMPS | LVD Bypass | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
1251 | PUN302 | IDMH106867 | DG | ID_PUNESOUTH | 459179 | KAKADE CITY | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 1 |  | 2 | 3
1252 | GRNR01 | IDMH105312 | DG | ID_NASHIK | 459883 | GIRNARE | NASHIK | ATS | MANOJ SINHA | BB | Zero Battery Backup | BB replaced | Closed | 2025-03-31 | 1 |  |  |  | 1
1253 | JLGN05 | IDMH102938 | DG | ID_AKOLA | 458243 | PIMPRALA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Obsolute model/Single LVD PP | New SMPS Req | Open | 2025-04-30 |  |  | 0.5 |  | 1
1254 | WRDI01 | IDMH100935 | DG | ID_AMRAVATI | 460030 | WARANDOLI | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS BER | SMPS Replaced | Reopen | 2025-03-31 | 0.5 |  | 1 | 2 | 3
1255 | TKNT01 | IDMH106838 | DG | ID_KOLHAPUR | 459543 | TALEKANTHE | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
1256 | HTNR01 | IDMH102958 | DG | ID_AURANGABAD | 460253 | HATNUR | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 2 |  |  | 2
1257 | AKLA41 | IDMH106936 | DG | ID_AKOLA | 505129 | DABKI ROAD | AKOLA | SAI | Vacant CE Akola | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1258 | PUN686 | IDMH105390 | NON DG | ID_PUNENORTH | 505521 | BHIM NAGAR- CHINCHAWAD | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1259 | PUN307 | IDMH106848 | DG | ID_PUNENORTH | 458969 | BHOSARI MIDC | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1260 | VING01 | IDMH106963 | DG | ID_SATARA | 459384 | VING | KOLHAPUR | SSS | VINOD SAWANT | SMPS | LVD bypassed | LVD replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1261 | PNVL04 | IDMH107011 | DG | ID_RAIGARH | 459661 | CHUGS PLOT, LONAWALA | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS controller Faulty | SMPS replaced | Closed | 2025-04-24 | 7 | 8 | 2 | 1 | 4
1262 | EXPH03 | IDMH106984 | DG | ID_RAIGARH | 565266 | OPEN PLOT KAMSHEET | PUNE-3 | ATS | PRATIK HULAVALE | Cable | SMPS to RRU VLTG Drop >3v | Cable replaced | Closed | 2025-02-28 |  | 1 |  |  | 1
1263 | KISH01 | IDMH101484 | DG | ID_NANDED | 464925 | KISHNUR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS controller faulty | Controller to be replaced | Open | 2025-05-07 | 1.5 | 2 | 1 | 1 | 4
1264 | HIN135 | INMH405543 | DG | ID_PUNESOUTH | 593725 | Club House Pune | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 2 | 0.5 | 2 | 3
1265 | ANGR13 | IDMH104670 | DG | ID_AHMEDNAGAR | 460351 | VAIDUWADI | AHMEDNAGAR | PTPL | NILESH NAGDEVE | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  |  | 1
1266 | PNDL01 | IDMH105429 | DG | ID_NASHIK | 459823 | PANDHURLI | NASHIK | ATS | SUBHASH SHINDE | SMPS | MCB Faulty | MCB replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
1267 | AURN24 | IDMH103089 | DG | ID_AURANGABAD | 460220 | SHAHGANJ | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1268 | DULE39 | IDMH108280 | DG | ID_NASHIK | 528924 | MOHADI UPNAGAR | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
1269 | NGP262 | IDMH108374 | DG | ID_NAGPUR | 571602 | MEHNDI BAGH BRIDGE | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1.5 |  | 1 | 2
1270 | NSK106 | IDMH105462 | DG | ID_NASHIK | 460004 | MUNGSARE | NASHIK | ATS | MANOJ SINHA | RRU | RRU faulty | Rectification done | Closed | 2025-02-23 | 1.5 | 0.5 |  |  | 2
1271 | PU2694 | INMH405723 | NON DG | ID_PUNENORTH | 594421 | Bhim Ngr_Airtel | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1272 | PU2505 | INMH405736 | NON DG | ID_PUNENORTH | 588056 | Police Station, Datta Mandir Rd, Wakad | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-01-17 | 2 |  |  |  | 1
1273 | RNBM01 | IDMH103226 | DG | ID_AKOLA | 458148 | RANICHE BAMBRUD | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
1274 | BHWL16 | IDMH107143 | NON DG | ID_AKOLA | 451537 | RAMMANDIRWRD_VF | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-05-15 | 2 |  | 0.5 | 1 | 3
1275 | DMGN04 | IDMH110554 | DG | ID_AMRAVATI | 531517 | DHAMANGAON RLY 2 | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Delta SMPS Controller faulty 4000 W | SMPS rectification done | Closed | 2025-03-31 | 6.5 | 2.5 | 1.5 |  | 3
1276 | CHIP06 | IDMH106132 | DG | ID_KOLHAPUR | 458952 | ALLORE | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | controller faulty/LVD bypassed | SMPS rectification planned | Open | 2025-04-20 | 0.5 | 1 |  |  | 2
1277 | NSK180 | IDMH107173 | DG | ID_NASHIK | 566687 | HIRAWADI | NASHIK | ATS | MANOJ SINHA | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
1278 | PUN845 | IDMH105491 | NON DG | ID_PUNENORTH | 459081 | HSBC GLT2 | PUNE-1 | INHOUSE | VIJAY KOLI | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-24 |  |  | 0.5 |  | 1
1279 | RGAR03 | IDMH105497 | DG | ID_PUNENORTH | 459492 | RAJGURUNAGAR WADA ROAD | PUNE-1 | ATS | SWAPNIL KARAD | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
1280 | VHWA01 | IDMH103319 | DG | ID_AURANGABAD | 459897 | VIHAMANDHWA | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | Update pending | Update pending | Update pending | Update pending | Update pending | 1.5 | 0.5 |  |  | 2
1281 | PUN257 | IDMH107229 | NON DG | ID_PUNESOUTH | 464871 | SYMTENTIC IBS | PUNE-2 | INHOUSE | VIPIN GUPTA | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 | 0.5 |  |  | 2
1282 | NERL02 | IDMH105542 | DG | ID_RAIGARH | 459992 | NERAL | PUNE-3 | ATS | ANANT TIDKE | BB | BB Backup Very Low | Plan for replacement | Open | 2025-04-30 |  |  | 0.5 |  | 1
1283 | PDHR01 | IDMH109295 | DG | ID_KOLHAPUR | 524690 | PAACH PANDHERI | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1284 | LNVL18 | IDMH109640 | DG | ID_RAIGARH | 521738 | TATA POWER GUEST HOUSE | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1285 | CHKN15 | IDMH105574 | NON DG | ID_PUNENORTH | 459667 | CHAKANGAON | PUNE-1 | ATS | SWAPNIL KARAD | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1286 | NDST01 | IDMH105603 | DG | ID_NASHIK | 460069 | NANDUR SHINGOTE | NASHIK | ATS | SUBHASH SHINDE | VIL Planned Activity | L900work done | NA | Closed | 2025-03-31 | 1 |  |  |  | 1
1287 | PU1288 | IDMH109657 | NON DG | ID_PUNENORTH | 465292 | TATA MOTORS ERC BUILDING PIMPRI | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | Smps Controller Faulty | SMPS to Change | Open | 2025-05-30 | 0.5 |  |  |  | 1
1288 | NGP173 | IDMH105654 | DG | ID_NAGPUR | 531036 | MAHAL | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS RM faulty | RM replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1289 | PAJM35 | IDMH106405 | DG | ID_GOA | 461325 | ARAMBOL | GOA | SSS | KISHOR SHIRSATH | Cable | common cable used for multiple RRU/Voltage drop>3v | Rquire saperate cable | Open | VIL Support Required | 0.5 |  |  |  | 1
1290 | ASKR01 | IDMH111490 | DG | ID_SOLAPUR | 459631 | ASHTA KASAR | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1291 | PAJ155 | IDMH106427 | NON DG | ID_GOA | 461383 | TAJ VIVANTA HOTEL | GOA | SSS | SURAJ PATIL | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1292 | MEHR01 | IDMH111666 | DG | ID_NASHIK | 458277 | MEHERGAON | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS Obsolute model | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 | 1 |  | 1 | 3
1293 | PAJM34 | IDMH106611 | DG | ID_GOA | 461327 | SIOLIM | GOA | SSS | KISHOR SHIRSATH | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 |  | 1 |  |  | 1
1294 | KMBJ01 | IDMH111709 | DG | ID_KOLHAPUR | 459717 | KUMBHOJ | KOLHAPUR | SSS | SANTOSH JADHAV | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1295 | JVLA01 | IDMH100396 | DG | ID_AMRAVATI | 460297 | JAVALA | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1296 | DVRS01 | IDMH103443 | DG | ID_KOLHAPUR | 505325 | DEVRASHTRE | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | controller faulty | New SMPS Req | Open | 2025-05-15 | 1 | 2.5 |  |  | 2
1297 | AKLW02 | IDMH112113 | DG | ID_NASHIK | 523346 | NANDURBAR_H | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS LVD faulty | SMPS rectification done | Closed | 2025-02-15 |  | 0.5 |  |  | 1
1298 | WLKR01 | IDMH105893 | NON DG | ID_KOLHAPUR | 459008 | WALAVALKAR HOSPITAL | KOLHAPUR | INHOUSE | VIVEK GOSAVI | Load Segregation | 1 RRU from critical | 1 RRH shifted & LVD settings | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1299 | PUN312 | IDMH105755 | DG | ID_PUNENORTH | 458776 | MHALUNGE COLLEGE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1300 | PUSL01 | IDMH106853 | DG | ID_AMRAVATI | 458010 | PUSLA | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS Controller faulty Delta 4000 W | SMPS Rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1301 | BHWL11 | IDMH107495 | DG | ID_AKOLA | 565760 | KENDRIYA VIDYALAYA,KANDARI | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-04-30 |  |  | 0.5 |  | 1
1302 | CPLI01 | IDMH100056 | DG | ID_SOLAPUR | 459053 | CHAPOLI | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
1303 | AURN59 | IDMH103557 | DG | ID_AURANGABAD | 464830 | WADGAON KOLHATI | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 | 2 | 4 |  |  | 2
1304 | PUN934 | IDMH107549 | DG | ID_PUNESOUTH | 522850 | WADGAON BUDRUK BYPASS | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | Smps Lvd Faulty | Rectification Done | Reopen | 2025-01-30 | 0.5 |  |  | 3 | 2
1305 | CHND93 | INMH002963 | DG | ID_CHANDRAPUR | 505165 | URJA NAGAR | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller and LLVD card faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  |  |  | 1
1306 | JUNR01 | IDMH105847 | DG | ID_RAIGARH | 460279 | JUNNAR | PUNE-1 | ATS | SWAPNIL KARAD | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 0.5 |  | 1 |  | 2
1307 | ISLA01 | IDMH100506 | DG | ID_NANDED | 505287 | ISLAPUR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS controller faulty | Controller to be replaced | Open | 2025-05-22 | 0.5 |  |  |  | 1
1308 | PUN947 | IDMH107609 | DG | ID_PUNENORTH | 566295 | WAGHOLI 2 | PUNE-1 | ATS | HARSHAL MAHAJAN | SMPS | SMPS BER | Smps replaced | Closed | 2025-01-30 | 3.5 |  |  |  | 1
1309 | LNVL27 | INMH400921 | DG | ID_RAIGARH | 530266 | KUSGAON | PUNE-3 | ATS | PRATIK HULAVALE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | Cable replaced | Closed | 2025-03-16 | 0.5 | 0.5 | 0.5 |  | 3
1310 | NGP472 | INMH401075 | NON DG | ID_NAGPUR | 575209 | MANKAPUR-3 | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1311 | BHRI01 | IDMH107657 | DG | ID_PUNESOUTH | 459678 | BHIVARI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 |  |  | 0.5 | 1 | 2
1312 | NRGL01 | INMHVF1646 | DG | ID_KOLHAPUR | 505373 | NARGOLI | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 1 |  |  | 2
1313 | AMBP01 | IDMH103970 | DG | ID_KOLHAPUR | 505297 | AMBAP | KOLHAPUR | SSS | SANTOSH JADHAV | RRU | RRU Faulty | Support req | Open | VIL Support Required |  |  | 0.5 |  | 1
1314 | CHAF01 | IDMH104045 | DG | ID_SATARA | 459289 | CHAFAL | KOLHAPUR | SSS | VINOD SAWANT | SMPS | LVD faulty | Plan for SMPS rectification | Open | 2025-04-30 | 2.5 |  |  |  | 1
1315 | TLGN01 | IDMH105936 | DG | ID_RAIGARH | 459736 | TALEGAON | PUNE-3 | ATS | PRATIK HULAVALE | RRU | RRU Faulty | RRU rectification done | Closed | 2025-03-31 |  |  | 1 |  | 1
1316 | BRWD01 | IDMH104337 | DG | ID_KOLHAPUR | 459720 | BAHIREWADI | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
1317 | AKLA06 | IDMH107748 | NON DG | ID_AKOLA | 565817 | JAIHIND CHOWK | AKOLA | SAI | Vacant CE Akola | SMPS | Smps Obsulate Model | Q1 SMPS Replacement planned | Open | 2025-04-30 |  | 1 |  | 2 | 2
1318 | NASK28 | IDMH105986 | DG | ID_NASHIK | 459919 | PAVAN NAGAR | NASHIK | ATS | SUBHASH SHINDE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required |  | 0.5 |  |  | 1
1319 | KLON01 | IDMH101510 | DG | ID_SOLAPUR | 458834 | KELGAON | LATUR | SAI | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1320 | PSOR01 | IDMH103721 | DG | ID_AURANGABAD | 458425 | PISHOR | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1321 | RSYN01 | IDMH106008 | DG | ID_RAIGARH | 570400 | PATALGANGA,RASAYANI | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1322 | PUN281 | IDMH104970 | DG | ID_PUNESOUTH | 459130 | APPA BALWANT CHOWK | PUNE-2 | ATS | AKSHAY SHELAR | Cable | VIL Cable underrated | Cable replacement req | Open | VIL Support Required | 1 |  |  |  | 1
1323 | PUN419 | IDMH106027 | DG | ID_PUNESOUTH | 459460 | SINHGAD MEDICAL COLLEGE | PUNE-2 | ATS | AKSHAY SHELAR | Cable | VIL Cable underrated | Cable replacement req | Open | VIL Support Required | 1 |  |  |  | 1
1324 | GUJR01 | IDMH105396 | DG | ID_KOLHAPUR | 459292 | GUJARWADI | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 1 |  |  |  | 1
1325 | NAND09 | IDMH106083 | DG | ID_NANDED | 565364 | NANDED MIDC | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 0.5 | 1 |  | 2
1326 | AURN39 | IDMH103830 | DG | ID_AURANGABAD | 505187 | OSMANPURA | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1327 | PUN855 | IDMH107829 | DG | ID_PUNENORTH | 521386 | DEHU SOUTH | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | Smps Controller Faulty | SMPS replaced | Closed | 2025-04-24 | 1 | 1 | 0.5 |  | 3
1328 | RVDN01 | IDMH106112 | DG | ID_RAIGARH | 459271 | REVDANDA | PUNE-2 | ATS | AMAY DORUGADE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1329 | NISA01 | IDMH107840 | DG | ID_RAIGARH | 459840 | NIMGAON SAVA | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-03 | 1.5 | 6.5 | 0.5 |  | 3
1330 | CHKR01 | IDMH101586 | DG | ID_SOLAPUR | 459352 | CHAKUR | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS LVD Faulty & Bypass | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
1331 | LNVL08 | IDMH106163 | DG | ID_RAIGARH | 503482 | INS_SHIVAJI LONAVALA | PUNE-3 | ATS | PRATIK HULAVALE | BB | BB cell faulty | BB Cell replaced | Closed | 2025-03-10 | 2 | 0.5 |  |  | 2
1332 | KNHE05 | INMH407032 | NON DG | ID_RAIGARH | 451514 | MAHINDRASTEEL_VF | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | Old absolue Model | SMPS To change | Open | 2025-05-30 |  | 0.5 |  |  | 1
1333 | PUN819 | IDMH106181 | NON DG | ID_PUNENORTH | 521132 | AKURDI GAVTHAN | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1334 | PUNE47 | IDMH105003 | NON DG | ID_PUNESOUTH | 459066 | PADMA PRABHA, NAVASHYADRI | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1335 | NDRD01 | IDMH105517 | DG | ID_NASHIK | 460363 | NANDURDI | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | LVD Bypass,Controller Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 2 | 1 |  | 6 | 3
1336 | JNSI01 | IDMH107944 | DG | ID_AKOLA | 458136 | JINSI RPT | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 | 0.5 | 1 |  |  | 2
1337 | HINJ23 | IDMH105588 | NON DG | ID_PUNESOUTH | 459050 | DLF SATYAM | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
1338 | NASK84 | IDMH106220 | DG | ID_NASHIK | 459955 | SHARANPUR LINK RD | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 |  | 1.5 |  | 2
1339 | GDGN01 | IDMH106221 | DG | ID_RAIGARH | 459898 | GHODEGAON | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 |  | 0.5 | 1 | 3
1340 | MLKD01 | IDMH102250 | DG | ID_AMRAVATI | 458111 | MALKHED | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Delta 4000 W LVD Card faulty | SMPS Rectification Done | Closed | 2025-03-07 | 0.5 |  | 0.5 |  | 2
1341 | DGHI07 | IDMH108093 | NON DG | ID_PUNENORTH | 527446 | SAWANT NAGAR_DIGHI. | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 2 | 0.5 | 1.5 | 3 | 4
1342 | PUN103 | IDMH106322 | DG | ID_PUNESOUTH | 459220 | MAYUR COLONY,KOTHRUD | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1343 | VKRM01 | IDMH107756 | NON DG | ID_RAIGARH | 459340 | VIKRAM ISPAT | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS Controller Faulty | SMPS replaced | Closed | 2025-04-24 |  | 1.5 |  | 3 | 2
1344 | KESP01 | IDMH108147 | DG | ID_AURANGABAD | 523939 | KESAPUR_NEW | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-05-22 | 0.5 |  |  |  | 1
1345 | PU1000 | IDMH108151 | NON DG | ID_PUNENORTH | 451316 | FUNDTECH_VF | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-15 | 1 | 0.5 |  |  | 2
1346 | KRMD01 | IDMH102317 | DG | ID_AURANGABAD | 460324 | KARMAD | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1347 | HTED01 | IDMH103853 | DG | ID_AKOLA | 458276 | HATED BK | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB cell faulty | Cell replaced | Closed | 2025-03-31 | 1 |  |  |  | 1
1348 | PUN470 | IDMH106402 | DG | ID_PUNESOUTH | 459214 | VEDANT NAGRI | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1349 | VIGN01 | IDMH106676 | DG | ID_RAIGARH | 459440 | VINEGAON | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS BLVD FAULTY | SMPS Replaced | Closed | 2025-04-24 | 2 |  | 0.5 | 3 | 3
1350 | KAKV06 | IDMH108428 | DG | ID_GOA | 531335 | KALMAT BIDYE_KANKAVLI | GOA | SSS | KISHOR SHIRSATH | Cable | DCDB to RRU voltage >2.5 V | cable replacement required | Open | VIL Support Required | 1.5 | 1 |  |  | 2
1351 | HIMA01 | IDMH102355 | DG | ID_NANDED | 459985 | HIMAYAT NAGAR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS controller faulty | SMPS controller needs to be changed | Open | 2025-05-15 | 0.5 | 1 |  | 1 | 3
1352 | BBBK01 | IDMH102391 | DG | ID_SOLAPUR | 459527 | BORGAON BK. | LATUR | SAI | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1353 | PUN613 | IDMH106450 | NON DG | ID_PUNESOUTH | 464866 | WONDER FUNKEY | PUNE-2 | INHOUSE | AKSHAY SHELAR | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1354 | PUN240 | IDMH106487 | DG | ID_PUNENORTH | 458762 | BHOSARI MIDC(ELECTRONIC SADAN) | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1355 | UMDI01 | IDMH102546 | DG | ID_KOLHAPUR | 459374 | UMADI | KOLHAPUR | SSS | VIVEK DESHPANDE | BB | Low Battery backup | BB upgradation done | Closed | 2025-03-31 |  | 0.5 | 0.5 |  | 2
1356 | HSUL01 | IDMH106518 | DG | ID_NASHIK | 460394 | HARSUL | NASHIK | ATS | MANOJ SINHA | RRU | RRU faulty | Rectification done | Closed | 2025-02-15 | 1 |  |  |  | 1
1357 | PAJ329 | IDMH108672 | NON DG | ID_GOA | 461379 | VEREM | GOA | SSS | SURAJ PATIL | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
1358 | DEUR01 | IDMH104989 | DG | ID_NASHIK | 457996 | DEUR BK | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-15 | 0.5 |  |  |  | 1
1359 | PUN397 | IDMH106573 | DG | ID_PUNENORTH | 458742 | EMPIRE ESTATE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
1360 | NASK04 | IDMH106584 | NON DG | ID_NASHIK | 459971 | MAHATMA NAGAR | NASHIK | ATS | MANOJ SINHA | RRU | RRU faulty | Rectification done | Closed | 2025-02-15 | 1 |  |  |  | 1
1361 | PUSD09 | IDMH108364 | DG | ID_AMRAVATI | 522525 | PN COLLEGE | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | smps controllar faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 1 |  | 2 | 2
1362 | NGP263 | IDMH108375 | DG | ID_NAGPUR | 531378 | KHASALA | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
1363 | PUN526 | IDMH106592 | DG | ID_PUNENORTH | 505115 | TATHAWADE | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1364 | KYLI01 | IDMH108398 | DG | ID_AMRAVATI | 523869 | KOYALI | AKOLA | SAI | ALI SHAH | SMPS | Delta 4000 W, BLVD and LVD and controller and SPD faulty | SMPS rectification done | Closed | 2025-04-09 | 0.5 | 0.5 | 0.5 | 3 | 4
1365 | EXPH06 | IDMH107005 | DG | ID_RAIGARH | 570341 | GUSALWADI | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1366 | PAJ381 | IDMH108793 | DG | ID_GOA | 522217 | BICHOLIM COW | GOA | SSS | SURAJ PATIL | SMPS | SMPS controller faulty | SMPS replacement done | Closed | 2025-01-08 | 0.5 |  |  |  | 1
1367 | CAUK01 | IDMH104529 | DG | ID_AURANGABAD | 460059 | CHAUKA | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | LLVD, Blvd card, controller faulty | SMPS Rectififiaction done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1368 | KRND01 | IDMH106652 | DG | ID_PUNENORTH | 459442 | KURKUNDI | PUNE-1 | ATS | SWAPNIL KARAD | Cable | DCDB to RRU Al cable underrated | cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
1369 | AKPD01 | IDMH105858 | DG | ID_NASHIK | 457962 | AKKALPADA | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 | 1 | 2
1370 | PNVL10 | IDMH107096 | DG | ID_RAIGARH | 458677 | PEN | PUNE-3 | ATS | ANANT TIDKE | Cable | DCDB to RRU cable long distance 30m | cable distane reduction req | Open | VIL Support Required | 1.5 | 0.5 |  |  | 2
1371 | MGON01 | IDMH103047 | DG | ID_KOLHAPUR | 505266 | MANGAON | KOLHAPUR | SSS | SANTOSH JADHAV | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1372 | NASK94 | IDMH106776 | DG | ID_NASHIK | 459950 | COLLEGE ROAD | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS LVD Faulty | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 | 1 |  |  | 2
1373 | MHAG01 | IDMH108575 | DG | ID_AMRAVATI | 523898 | MAHAGAON_A | AKOLA | SAI | ALI SHAH | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-15 |  | 0.5 | 0.5 |  | 2
1374 | KJMB01 | IDMH111793 | DG | ID_NASHIK | 458436 | KHADAKJAMB | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1375 | SRDN01 | IDMH103062 | DG | ID_KOLHAPUR | 459594 | SHIRDHON | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1376 | PUN244 | IDMH105556 | DG | ID_PUNENORTH | 458749 | CHAROLIGAON | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  |  |  | 1
1377 | NGDM01 | IDMH107189 | DG | ID_KOLHAPUR | 505257 | NIGVE DHUMALA | KOLHAPUR | SSS | SANTOSH JADHAV | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 | 0.5 |  | 2
1378 | KJDI01 | IDMH106830 | DG | ID_RAIGARH | 459362 | KARANJADI | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  |  |  | 1
1379 | PUNE41 | IDMH104334 | DG | ID_PUNENORTH | 459144 | C R AGAWAL BLDG. | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-13 | 0.5 | 1 |  |  | 2
1380 | PUNE20 | IDMH105351 | DG | ID_PUNESOUTH | 459149 | VISHWESHWAR BANK | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1381 | SKHR01 | IDMH103123 | DG | ID_SATARA | 459288 | SAKHARWADI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1382 | JALN53 | INMH405747 | NON DG | ID_AURANGABAD | 586275 | Income Tax Colony_Airtel | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | SMPS | SMPS Backplane faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1383 | HINJ04 | IDMH106925 | DG | ID_PUNESOUTH | 459023 | TAMANNA EXECUTIVE | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1384 | WTUR01 | IDMH108735 | DG | ID_AURANGABAD | 505356 | VATUR PHATA | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | SMPS | Smps Controller Faulty | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1385 | PUN292 | IDMH106945 | DG | ID_PUNESOUTH | 464878 | BANER | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 |  | 3.5 |  |  | 1
1386 | BDGN02 | IDMH108776 | DG | ID_AURANGABAD | 522668 | BHADGAON_3 | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan for rectification | Open | 2025-04-30 |  | 2 |  |  | 1
1387 | PUN199 | IDMH106413 | DG | ID_PUNESOUTH | 459062 | KATRAJ DEHU ROAD | PUNE-2 | ATS | VIPIN GUPTA | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1388 | PUNE46 | IDMH106967 | DG | ID_PUNENORTH | 458792 | GAJANAN COMPLEX | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1389 | SONL01 | IDMH107383 | DG | ID_KOLHAPUR | 459437 | SONYAL RPT | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | controller faulty | Controller to be replaced | Open | 2025-05-22 | 0.5 |  |  |  | 1
1390 | PUN769 | IDMH108800 | DG | ID_PUNESOUTH | 464809 | NEAR NIRMAL TOWNSHIP--ANANDNAGAR | PUNE-2 | ATS | AKSHAY SHELAR | Cable | DCDB to RRU Underrated cable vtg drop 2.9v | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
1391 | NSK239 | IDMH110575 | DG | ID_NASHIK | 577377 | MAXHEAL PHRMCETICL | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS controller faulty | Plan for SMPS rectification | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1392 | PAJ441 | IDMH110700 | DG | ID_GOA | 523287 | SUKTALI | GOA | SSS | SUNIL TAMSE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 |  | 2 | 0.5 |  | 2
1393 | KAPD01 | IDMH106256 | DG | ID_KOLHAPUR | 459601 | KAPADGAON | KOLHAPUR | SSS | VIVEK GOSAVI | RRU | RRU Issue | VIL Support require | Open | VIL Support Required | 1 |  |  |  | 1
1394 | PNSK01 | IDMH105437 | DG | ID_RAIGARH | 460017 | PETH | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS BER | Plan for SMPS Replacement | Open | 2025-04-30 | 2.5 |  |  |  | 1
1395 | PUNE97 | IDMH107101 | DG | ID_PUNESOUTH | 459195 | KRISHNA DINING HALL | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 |  |  | 1 |  | 1
1396 | GTNJ02 | IDMH108902 | DG | ID_AMRAVATI | 502734 | GHATANJI 2 | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Smps Controller And Lvd Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1397 | PUN868 | IDMH112399 | DG | ID_PUNESOUTH | 521489 | SURESH NAGAR | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-09 | 6 | 1 | 2.5 | 1 | 4
1398 | CHKR02 | IDMH107146 | DG | ID_SOLAPUR | 565675 | CHAKUR MARKET | LATUR | PTPL | SUDHIR AGHE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-20 | 0.5 | 2.5 |  |  | 2
1399 | PTRD02 | IDMH107159 | NON DG | ID_AHMEDNAGAR | 460286 | KASBA PETH | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1400 | NSK185 | IDMH108942 | DG | ID_NASHIK | 520677 | DEOLALI ROAD-2 | NASHIK | ATS | SUBHASH SHINDE | BB | BB cell faulty | Plan for cell replacement | Open | 2025-04-30 | 1.5 |  |  |  | 1
1401 | PUNE51 | IDMH107228 | NON DG | ID_PUNENORTH | 458786 | TELCO | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 0.5 | 2.5 |  | 3
1402 | KHOP01 | IDMH108122 | DG | ID_RAIGARH | 567873 | SHRI RAM MANGAL KARYALAYA | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1403 | NGP287 | IDMH109102 | DG | ID_NAGPUR | 565467 | MEDICAL CHOWK | NAGPUR | SAI | MILIND RAMTEKE | BB | Zero Battery backup | Plan for BB upgradation | Open | 2025-04-30 |  |  | 0.5 |  | 1
1404 | KNHN01 | IDMH111239 | DG | ID_NAGPUR | 458312 | KANHAN | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 3 | 1
1405 | PU1456 | IDMH100880 | DG | ID_PUNENORTH | 465835 | ARMY CANTONMENT, AUNDH | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
1406 | VDNG01 | IDMH103306 | DG | ID_KOLHAPUR | 458654 | VADANGE | KOLHAPUR | SSS | SANTOSH JADHAV | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1407 | PUN233 | IDMH106729 | NON DG | ID_PUNESOUTH | 459186 | ICC-ITC | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Backplane faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1408 | KAJN02 | IDMH107386 | DG | ID_NAGPUR | 566010 | KARANJA GHATGE | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1409 | SOLP65 | IDMH107387 | DG | ID_SOLAPUR | 565781 | SHIVAGANGA NAGAR | SOLAPUR | PTPL | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1410 | PUN990 | IDMH107388 | DG | ID_PUNENORTH | 566722 | SANT TUKARAM NGR PUNE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1411 | PUN207 | IDMH107038 | DG | ID_PUNESOUTH | 459059 | BALEWADI | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | BB upgradation done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1412 | AUR142 | IDMH107391 | DG | ID_AURANGABAD | 573811 | RAM MANDIR | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-02-22 | 0.5 | 1.5 |  |  | 2
1413 | PU2032 | IDMH109235 | NON DG | ID_PUNENORTH | 526307 | INDRAYANI NAGAR IV. | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | Smps Controller Faulty | SMPS Replaced | Closed | 2025-01-30 | 1.5 |  |  |  | 1
1414 | BAGN01 | IDMH101897 | DG | ID_SOLAPUR | 459574 | BABHALGAON | LATUR | SAI | SUDHIR AGHE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1415 | ALBG14 | IDMH107438 | DG | ID_RAIGARH | 505447 | SASAVANE | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1416 | GOND09 | IDMH107454 | DG | ID_CHANDRAPUR | 567179 | NEAR HOTEL ANNAPURNA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS Controller faulty | SMPS Replaced | Closed | 2025-03-16 | 0.5 | 0.5 | 0.5 |  | 3
1417 | PUN818 | IDMH106063 | DG | ID_PUNESOUTH | 451286 | DAHANUKARCOLY_VF | PUNE-2 | ATS | AKSHAY SHELAR | Cable | DCDB to RRU voltage >3.5V underrated cu cable | cable replacement required | Open | VIL Support Required | 1.5 | 1.5 | 1.5 |  | 3
1418 | PNAD01 | IDMH107460 | DG | ID_RAIGARH | 458820 | POINAD | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-31 | 1 |  |  |  | 1
1419 | JLGN69 | INMHVF1392 | DG | ID_AKOLA | 565593 | MURALI MANOHAR HOTEL,NH-6 | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-31 | 2 | 1.5 | 0.5 |  | 3
1420 | NDBR13 | IDMH109339 | DG | ID_NASHIK | 565940 | GIRIVIHAR SOCIETY | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-04-09 | 1.5 | 1 | 1.5 | 1 | 4
1421 | PUN262 | IDMH106069 | DG | ID_PUNESOUTH | 459561 | KHANAPUR | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS RM faulty | RM replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1422 | AMVT59 | IDMH109390 | DG | ID_AMRAVATI | 572557 | UNIVERSITY_AMRAVATI | AKOLA | SAI | BHUSHAN BAREKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 | 1 | 2
1423 | GHOT01 | IDMH106650 | DG | ID_NASHIK | 460076 | GHOTI | NASHIK | ATS | SUBHASH SHINDE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 0.5 | 1 |  |  | 2
1424 | PUN922 | IDMH107569 | DG | ID_PUNENORTH | 522822 | RAKSHAK NGR PHASE 2A | PUNE-1 | ATS | HARSHAL MAHAJAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1425 | HINJ38 | IDMH112393 | NON DG | ID_PUNESOUTH | 459041 | DLF BLOCK 4 | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | SMPS | SMPS BER | SMPS to Replace | Open | 2025-05-15 | 1 |  | 1 | 1 | 3
1426 | PUN989 | IDMH107620 | NON DG | ID_PUNENORTH | 523141 | VISHALNAGAR KALEWADI | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1427 | PUN670 | IDMH105846 | NON DG | ID_PUNESOUTH | 459244 | SHARADA CHAMBER | PUNE-2 | ATS | RAHUL TUPARE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1428 | MASU01 | IDMH109780 | DG | ID_KOLHAPUR | 528539 | MHASURLI | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | LVD bypassed | SMPS replaced | Closed | 2025-04-24 | 1 | 0.5 |  |  | 2
1429 | PU1146 | IDMH109505 | DG | ID_PUNESOUTH | 521291 | DHARYESHWAR | PUNE-2 | ATS | AKSHAY SHELAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-15 |  | 1 | 0.5 |  | 2
1430 | PU1377 | IDMH110275 | DG | ID_PUNENORTH | 527995 | KALBHOR WASTI | PUNE-1 | ATS | HARSHAL MAHAJAN | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1.5 | 1.5 | 0.5 |  | 3
1431 | TLTU01 | INMH001476 | DG | ID_NAGPUR | 458396 | TALEGAON (TALATULE) | NAGPUR | SAI | VIVEK GANJARE | SMPS | LLVD Card Faulty | NFA Raised | Open | 2025-04-20 | 2 |  | 0.5 | 1 | 3
1432 | MNVL01 | IDMH107715 | DG | ID_RAIGARH | 459873 | MANIVALI | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1433 | KBHM04 | IDMH108154 | DG | ID_PUNENORTH | 458866 | RIETER INDIA_COW_KBHM04_COW | PUNE-1 | SAI | HARSHAL MAHAJAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1434 | BRDL01 | IDMH109619 | DG | ID_RAIGARH | 525442 | BHARADKHOL_NEW | PUNE-2 | ATS | AMAY DORUGADE | BB | BB cell faulty | Cell replaced | Closed | 2025-04-24 | 1 | 1 | 0.5 |  | 3
1435 | CHPR01 | IDMH106347 | DG | ID_AURANGABAD | 458607 | CHINCHPUR | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | SMPS BER | New SMPS Req | Open | 2025-05-30 |  | 0.5 |  |  | 1
1436 | SIRR01 | IDMH102915 | DG | ID_PUNENORTH | 459500 | SHIRUR, MAHALAXMI BLDG | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  | 1 | 2
1437 | PUN901 | IDMH107775 | DG | ID_PUNESOUTH | 521601 | KALE BORATE ROAD _B | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 1 | 1.5 |  | 3
1438 | AMVT56 | IDMH109687 | DG | ID_AMRAVATI | 566200 | JAIRAM NAGAR, AMARAVATI | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | Smps Controller Faulty | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1439 | NAND23 | IDMH101302 | DG | ID_NANDED | 460317 | WADI BK | LATUR | PTPL | Vacant CE Latur | Cable | SMPS to BTS cable underrated voltage drop >2.6V | Plan for cable replacement | Open | 2025-04-20 | 5.5 | 2.5 | 1 | 3 | 4
1440 | PU1067 | IDMH107820 | DG | ID_PUNENORTH | 566716 | SURULE NAGAR_PIMPLE GURAV | PUNE-2 | ATS | VIPIN GUPTA | RRU | RRU faulty | RRU replaced | Closed | 2025-03-31 |  | 0.5 | 0.5 |  | 2
1441 | AMVT67 | IDMH109778 | DG | ID_AMRAVATI | 525832 | SRPF, AMRAVATI | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1442 | MLGN15 | IDMH107863 | DG | ID_NASHIK | 566047 | SHRI BALAJI MANDHIR,MALEGAON | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1443 | ACPR05 | IDMH109792 | DG | ID_AMRAVATI | 531507 | ACHALPUR 2 | AKOLA | SAI | BHUSHAN BAREKAR | SMPS | SMPS BER | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1444 | BDRV06 | IDMH109794 | DG | ID_CHANDRAPUR | 567104 | BHADRAVATI NTPC | NAGPUR | SAI | GANESH DANDALWAR | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 0.5 | 0.5 | 0.5 |  | 3
1445 | NGP242 | IDMH107887 | DG | ID_NAGPUR | 565438 | CHATRAPATI NAGAR | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1446 | ALBG16 | IDMH107895 | DG | ID_RAIGARH | 531816 | KOPROLI | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-13 | 0.5 | 0.5 |  |  | 2
1447 | KOL111 | IDMH110988 | DG | ID_KOLHAPUR | 566339 | MARKET YARD, KOLHAPUR | KOLHAPUR | SSS | RITESH RANGOLE | SMPS | LVD bypassed | Eltek PP replacement reqd | Open | 2025-05-07 | 1 | 1 | 0.5 |  | 3
1448 | DIGI01 | IDMH107916 | DG | ID_RAIGARH | 458614 | DIGHI | PUNE-2 | ATS | AMAY DORUGADE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
1449 | LNVL19 | IDMH111083 | DG | ID_RAIGARH | 521880 | GOLD VALLEY LONAVALA | PUNE-3 | ATS | PRATIK HULAVALE | Cable | SMPS to RRU VLTG Drop >3v | cable to replace | Open | VIL Support Required | 1 |  |  | 1 | 2
1450 | PUN852 | IDMH107936 | DG | ID_PUNESOUTH | 522092 | PUNE UNIVERSITY 04 - IBB BUILDING | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
1451 | WLCN01 | IDMH107971 | DG | ID_PUNESOUTH | 505156 | WALCHAND NAGAR | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  | 1 | 2 | 3
1452 | NGAO02 | IDMH109891 | NON DG | ID_PUNESOUTH | 459407 | ULTRA TECH(NAIGAON) | PUNE-1 | SAI | VIJAY KOLI | SMPS | Not OK - Controller & LVD Faulty | SMPS replaced | Closed | 2025-04-24 | 2 | 1.5 | 0.5 |  | 3
1453 | WADN01 | IDMH108065 | DG | ID_AURANGABAD | 523889 | WADHONA | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1454 | KHLP01 | IDMH108066 | DG | ID_AURANGABAD | 523980 | KHALAPURI NEW | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1455 | LBPR01 | IDMH104033 | DG | ID_PUNESOUTH | 458622 | LONI BHAPKAR | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1456 | PU1124 | IDMH109960 | DG | ID_PUNENORTH | 531699 | HP PETROL PUMP, PUNA | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | SMPS | SMPS BER | SMPS Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1457 | PU1128 | IDMH109961 | NON DG | ID_PUNENORTH | 465344 | CAPGEMINI TALWADE | PUNE-3 | ATS | PRATIK HULAVALE | RRU | RRU Faulty | RRU rectification done | Closed | 2025-03-31 |  |  | 1 |  | 1
1458 | BDLE01 | IDMH104273 | DG | ID_KOLHAPUR | 459714 | BHADOLE | KOLHAPUR | SSS | SANTOSH JADHAV | SMPS | SMPS LVD Faulty TT NO 250228CM3090218 | Plan for rectification | Open | 2025-05-15 |  | 0.5 | 0.5 | 1 | 3
1459 | PUN445 | IDMH105053 | DG | ID_PUNESOUTH | 459507 | KATRAJ TUNNEL II | PUNE-2 | ATS | RAHUL TUPARE | RRU | VIL RRU Malfunctioning | RRU Replaced | Closed | 2025-02-28 |  | 1.5 |  |  | 1
1460 | PUN983 | IDMH108125 | DG | ID_PUNENORTH | 566954 | LOHGAON3 | PUNE-1 | ATS | HARSHAL MAHAJAN | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1461 | PUN466 | IDMH105112 | DG | ID_PUNESOUTH | 459063 | BALEWADI STADIUM | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-04-24 |  | 0.5 |  |  | 1
1462 | BRMT17 | IDMH104102 | DG | ID_PUNESOUTH | 566365 | RADHA GOVIND RESIDENCY | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1463 | MIRJ08 | IDMH104279 | DG | ID_KOLHAPUR | 459709 | GANESH TALAV | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1464 | PUN177 | IDMH105161 | DG | ID_PUNESOUTH | 459231 | GANESH PETH, RAVIWAR PETH | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1465 | CHKN73 | IDMH110129 | DG | ID_PUNENORTH | 552735 | CHAKAN GAON | PUNE-1 | ATS | SWAPNIL KARAD | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-04-30 |  | 0.5 |  |  | 1
1466 | GRDE01 | IDMH104129 | DG | ID_PUNESOUTH | 459618 | GARADE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 2 | 1 | 0.5 |  | 3
1467 | PUN326 | IDMH106455 | DG | ID_PUNESOUTH | 464797 | GANDHI CHOWK | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1468 | GVRI04 | IDMH110158 | DG | ID_AURANGABAD | 465474 | SHIKSHAK COLONY | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  | 0.5 |  | 2
1469 | PUNE69 | IDMH105353 | DG | ID_PUNESOUTH | 459135 | AMAR SAKET, SWARGATE | PUNE-2 | ATS | RAHUL TUPARE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required | 0.5 |  |  |  | 1
1470 | PUN271 | IDMH104243 | NON DG | ID_PUNESOUTH | 459342 | VASANTDATA SUGAR INSTITUTE | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
1471 | ADSG01 | IDMH108406 | DG | ID_AURANGABAD | 523979 | ADGAON SARAK NEW | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1472 | NGP406 | IDMH110225 | DG | ID_NAGPUR | 526480 | SRPF, NAGPUR | NAGPUR | SAI | KAILASH POKALE | SMPS | SMPS controller faulty | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 | 2 |  |  | 2
1473 | PUN955 | IDMH108431 | NON DG | ID_PUNESOUTH | 451445 | HEAVENPARK_VF | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1474 | CHKN48 | IDMH108447 | DG | ID_PUNENORTH | 459727 | MINDA | PUNE-1 | ATS | SWAPNIL KARAD | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
1475 | MRGN01 | IDMH104275 | DG | ID_PUNESOUTH | 459745 | MORGAON | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | BB cell faulty | BB cell replaced | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1476 | PCRA03 | IDMH108501 | DG | ID_AURANGABAD | 531570 | PACHORA TOWN | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB Cell faulty | Cell replaced | Reopen | 2025-03-16 |  | 0.5 | 1 | 1 | 3
1477 | BHAN15 | IDMH108568 | DG | ID_CHANDRAPUR | 567158 | SHAHU NAGAR | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS BER | SMPS replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1478 | JLGN26 | IDMH107040 | DG | ID_AKOLA | 565596 | M/S GOPICHAND OIL INDUSTRIES, JALGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-20 |  | 0.5 | 1 |  | 2
1479 | SANG05 | IDMH104505 | NON DG | ID_KOLHAPUR | 459705 | SHIVAJINAGAR | KOLHAPUR | SSS | VIVEK DESHPANDE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1480 | PBNI05 | IDMH107142 | DG | ID_NANDED | 460167 | NEW MONDHA | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | BB | Zero battery backup | BB Installed | Closed | 2025-02-15 | 2.5 |  |  |  | 1
1481 | LNGN01 | IDMH110339 | DG | ID_RAIGARH | 465484 | LAKHANGAON | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-04-09 | 0.5 | 1 | 0.5 | 1 | 4
1482 | LNVL28 | INMH400797 | NON DG | ID_RAIGARH | 530320 | BHAGARWADI | PUNE-3 | ATS | PRATIK HULAVALE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-04-24 | 0.5 |  |  | 3 | 2
1483 | PAJ421 | INMH406904 | DG | ID_GOA | 522216 | APRANT MINES | GOA | SSS | SUNIL TAMSE | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1484 | NAND22 | IDMH101377 | DG | ID_NANDED | 460385 | BALI RAM PUR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS Obsolute model/Singal Lvd | SMPS replaced | Closed | 2025-04-24 | 1 |  |  |  | 1
1485 | MIH104 | INMH400924 | NON DG | ID_PUNESOUTH | 530101 | HYATT PLACE, HINJAWADI | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 1 | 1 | 2
1486 | JLGN33 | IDMH108759 | DG | ID_AKOLA | 571553 | NEHRU NAGAR_JALGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Zero Battery Backup | BB replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1487 | GNPU01 | IDMH110519 | DG | ID_AURANGABAD | 505183 | GANGAPUR DAHEGAON | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | SMPS BER | Plan for SMPS Replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1488 | BAWD01 | IDMH103479 | DG | ID_SATARA | 459357 | BAWADA | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS Slot Faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1489 | SSWD02 | IDMH104371 | DG | ID_PUNESOUTH | 459621 | SASWAD II | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | BB cell faulty | BB cell replaced | Open | 2025-05-30 |  | 0.5 |  |  | 1
1490 | NGPR06 | IDMH100248 | NON DG | ID_NAGPUR | 458354 | KADBI CHOWK | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1491 | RJUI01 | IDMH104621 | DG | ID_SATARA | 459425 | RAJURI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 1 | 0.5 |  |  | 2
1492 | BRAD01 | IDMH100725 | DG | ID_NANDED | 460250 | BARAD | LATUR | PTPL | RAJKUMAR ALANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 4 | 1
1493 | ANKT01 | IDMH110676 | DG | ID_NASHIK | 523867 | ANKUTE | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS Faulty | SMPS Replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
1494 | BLLR04 | IDMH109008 | DG | ID_CHANDRAPUR | 500936 | BALLARPUR-2 | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
1495 | JYKD01 | IDMH104061 | DG | ID_NASHIK | 458149 | JAIKHEDA | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1496 | AUR129 | IDMH107680 | DG | ID_AURANGABAD | 532930 | SARA PRIDE | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | controller faulty | Controller to be replace | Open | 2025-04-30 |  | 0.5 |  |  | 1
1497 | PAJ170 | IDMH105421 | NON DG | ID_GOA | 461441 | JOECONS GARDEN | GOA | SSS | SUNIL TAMSE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 2 |  |  | 2
1498 | PU1152 | IDMH109124 | NON DG | ID_PUNENORTH | 527608 | OLD SANGHVI IV | PUNE-2 | INHOUSE | VIPIN GUPTA | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 3 | 1
1499 | NASK33 | IDMH105030 | DG | ID_NASHIK | 464887 | SAYYAD PIMPRI | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | Controller Faulty | SMPS Rectification Require | Open | 2025-05-07 | 0.5 | 1 | 0.5 |  | 3
1500 | TTNE01 | IDMH108415 | DG | ID_NASHIK | 523968 | TITANE | NASHIK | ATS | NILESH BHAVSAR | SMPS | Controller Faulty | SMPS Rectification done | Closed | 2025-01-30 | 1.5 |  |  |  | 1
1501 | NGP427 | IDMH110753 | NON DG | ID_NAGPUR | 576363 | HUDKESHWAR POLICE STATION | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS RM Faulty | RM replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1502 | PU2506 | INMH405433 | NON DG | ID_PUNENORTH | 587831 | Krantiveer Nagar, Pawar Nagar, Pimpri-Chinchwad | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | Controller Faulty | SMPS replaced | Closed | 2025-04-24 |  | 3 |  | 1 | 2
1503 | PU1116 | IDMH109241 | DG | ID_PUNESOUTH | 566826 | VIKRAM APARTMENT | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1504 | NGAN01 | IDMH106043 | DG | ID_NASHIK | 460144 | NAIGAON | NASHIK | ATS | SUBHASH SHINDE | RRU | VIL RRU Faulty | RRU Replacement Req | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
1505 | PAJM50 | IDMH105748 | NON DG | ID_GOA | 461377 | MOBOR(VELIM) | GOA | SSS | SURAJ PATIL | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
1506 | NSK158 | IDMH106525 | DG | ID_NASHIK | 505228 | GANGAPUR | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1507 | PUN411 | IDMH105695 | DG | ID_PUNESOUTH | 459506 | KATRAJ TUNNEL, AMBEGAON | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1508 | DRMB06 | INMH404764 | DG | ID_NANDED | 505137 | DHARMABAD | LATUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1509 | AUR167 | IDMH109442 | NON DG | ID_AURANGABAD | 460370 | MYLAN LAB | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1510 | WAII01 | IDMH105779 | DG | ID_SATARA | 459418 | WAI | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1511 | CHKN66 | IDMH109457 | NON DG | ID_PUNENORTH | 465320 | BADVE ENGINEERING KHALUMBRE | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1512 | CHKN47 | IDMH109556 | DG | ID_PUNENORTH | 576874 | MINDA SWITH CHAKAN | PUNE-1 | ATS | SWAPNIL KARAD | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1513 | BRSI09 | IDMH109571 | DG | ID_SOLAPUR | 526213 | CANCER HOSPITAL-BARSHI. | SOLAPUR | PTPL | BALASAHEB KADAM | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1514 | PUN212 | IDMH106666 | DG | ID_PUNESOUTH | 459127 | MHATRE BRIDGE | PUNE-2 | ATS | AKSHAY SHELAR | Cable | Underated cable From DCDB To rru | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1515 | BPGN01 | IDMH105019 | DG | ID_PUNESOUTH | 459563 | BOPGAON | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 |  |  | 1 |  | 1
1516 | NSRP01 | IDMH105786 | DG | ID_PUNESOUTH | 565873 | NASARAPUR OPEN PLOT | PUNE-2 | ATS | RAHUL TUPARE | RRU | RRU faulty | RRU replaced | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1517 | BHWL26 | IDMH111013 | DG | ID_AKOLA | 522530 | BHUSAWAL_4 | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | load LVD faulty 2 | Plan for rectification | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
1518 | PU1205 | IDMH109717 | NON DG | ID_PUNENORTH | 572556 | VED APPARTMENT (MOUNT VIEW SOCEITY_PASHAN) | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
1519 | SHID01 | IDMH105839 | DG | ID_PUNESOUTH | 459571 | KATRAJ TUNNEL III | PUNE-2 | ATS | RAHUL TUPARE | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1520 | PUN710 | IDMH105948 | DG | ID_PUNESOUTH | 459159 | SOMESHWARWADI (BANER) - PUNE | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1521 | PU1231 | IDMH109771 | NON DG | ID_PUNENORTH | 458744 | FORCE MOTORS_COW14 | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1522 | UBRL01 | IDMH105856 | DG | ID_KOLHAPUR | 459786 | UMBARLE | KOLHAPUR | SSS | VIVEK GOSAVI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1523 | PU1256 | IDMH109836 | DG | ID_PUNENORTH | 524978 | PINNACLE GULMOHAR | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller Faulty | SMPS rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1524 | PUNE59 | IDMH109875 | NON DG | ID_PUNENORTH | 573368 | JAI APP_PRADIKARAN | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1525 | NGP291 | IDMH112181 | DG | ID_NAGPUR | 572723 | FRIENDS COLONY 4 | NAGPUR | SAI | LEELADHAR BHOSKAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 |  | 3.5 |  | 1 | 2
1526 | NSK281 | IDMH100153 | DG | ID_NASHIK | 575245 | DATTA NAGAR_NASIK | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-04-30 |  | 0.5 |  |  | 1
1527 | JALN27 | IDMH108571 | DG | ID_AURANGABAD | 566102 | ROOPAM CONCAST - 2 | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 | 1 |  | 2
1528 | PU1266 | IDMH109980 |  | ID_PUNENORTH | 459347 | HDFC BANK, BUND GARDEN RD | PUNE-2 | NonActive | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending | 3.5 | 1 |  |  | 2
1529 | PUNE07 | IDMH105164 | DG | ID_PUNENORTH | 459226 | SHAILESHWAR SOC. | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 |  | 0.5 | 1.5 |  | 2
1530 | ASSH01 | IDMH111303 | DG | ID_CHANDRAPUR | 451401 | CHANDANKHEDA ASHTA | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1531 | KNHN02 | IDMH110059 | DG | ID_NAGPUR | 567119 | KANHAN-2 NAGPUR | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1532 | HING01 | IDMH111320 | DG | ID_NAGPUR | 458116 | HINGANGHAT | NAGPUR | SAI | VIVEK GANJARE | RRU | 1 RRU Faulty | RRU replaced | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1533 | CHIP04 | IDMH106430 | NON DG | ID_KOLHAPUR | 458911 | CHIPLUN HIGHWAY | KOLHAPUR | SSS | VIVEK GOSAVI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1534 | WADU01 | IDMH105349 | DG | ID_PUNENORTH | 458859 | WADHU | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
1535 | MNGH01 | IDMH111390 | DG | ID_AMRAVATI | 451421 | MANGKINI | AKOLA | SAI | DHANRAJ NIBALKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1536 | TKMD01 | IDMH111415 | DG | ID_CHANDRAPUR | 451526 | SHENGAON/TEKAMANDWA | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 0.5 | 1 | 2
1537 | JLGN37 | IDMH108861 | DG | ID_AKOLA | 565591 | SARASWATI NAGAR, NERI NAKA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-20 |  | 0.5 | 0.5 |  | 2
1538 | PUN400 | IDMH106451 | DG | ID_PUNENORTH | 464793 | DAPODI | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1539 | KSPR01 | IDMH111468 | DG | ID_AURANGABAD | 460280 | KESAPURI | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS BER | Replacement Pending | Open | 2025-05-30 |  | 1 |  |  | 1
1540 | SDON01 | IDMH111470 | DG | ID_NANDED | 460084 | SHIRADHON | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Obsolute model | Plan for SMPS replacement | Open | 2025-05-30 | 0.5 |  |  |  | 1
1541 | NASK35 | IDMH109936 | DG | ID_NASHIK | 459937 | PANDIT COLONY_NASK35 | NASHIK | ATS | MANOJ SINHA | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1542 | PIPL01 | IDMH110027 | DG | ID_NASHIK | 525900 | PIMPALGAON_USO | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1543 | PBNI31 | IDMH110220 | DG | ID_NANDED | 531324 | GURUMITRA COLONY | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1544 | AUR181 | IDMH109465 | DG | ID_AURANGABAD | 566090 | SANJAY NAGAR | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1545 | SAGM16 | IDMH110228 | DG | ID_AHMEDNAGAR | 566982 | OPEN PLOT GULEWADI | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1546 | PU1373 | IDMH110240 | NON DG | ID_PUNESOUTH | 577582 | GANGA KINGSTON REPEATER | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1547 | BUDA01 | IDMH111522 | DG | ID_SOLAPUR | 459680 | BUDHADA | LATUR | SAI | SUDHIR AGHE | SMPS | SMPS Obsolute model | Plan for replacement | Open | 2025-05-07 | 1 | 1 | 1 |  | 3
1548 | PUN293 | IDMH106684 | NON DG | ID_PUNESOUTH | 459178 | AUNDHGAON | PUNE-2 | ATS | VIPIN GUPTA | SMPS | RM faulty | RM replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1549 | PUN109 | IDMH106866 | DG | ID_PUNESOUTH | 459191 | ITI ROAD, AUNDH | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Cell faulty | Plan for cell replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1550 | KHED01 | IDMH106720 | DG | ID_KOLHAPUR | 459785 | KHED | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | LVD faulty | LVD & controller to be replaced | Open | 2025-04-20 | 0.5 | 0.5 |  |  | 2
1551 | JLGN56 | IDMH110308 | DG | ID_AKOLA | 575746 | DAULAT NAGAR_JALGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Zero Battery Backup | BB replaced | Closed | 2025-03-31 | 1.5 |  | 1 |  | 2
1552 | PU1349 | IDMH110317 | NON DG | ID_PUNESOUTH | 575268 | BHOSALE NAGAR-RANGE HILLS | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
1553 | PU1041 | IDMH110325 | NON DG | ID_PUNESOUTH | 577370 | KOTHRUD BUS STAND | PUNE-2 | INHOUSE | AKSHAY SHELAR | BB | Battery backup 30 min | Plan For new BB replace | Open | 2025-05-30 |  |  | 1 |  | 1
1554 | AURN66 | IDMH111588 | DG | ID_AURANGABAD | 505347 | WALUJ MIDC 3 (PUSHPAK PLASTICS) | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-04-30 | 0.5 |  |  |  | 1
1555 | KOL101 | IDMH111597 | NON DG | ID_KOLHAPUR | 528826 | NIRANKARI COLONY_01 | KOLHAPUR | SSS | SANTOSH JADHAV | RRU | RRU Faulty | Support req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
1556 | BHWL17 | IDMH109833 | DG | ID_AKOLA | 531118 | BHUSAWAL_8 | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1557 | BHWL25 | IDMH110337 | DG | ID_AKOLA | 505215 | BHUSAVAL MARKET | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1558 | KOLP70 | IDMH106805 | DG | ID_KOLHAPUR | 565944 | CYBER COLLEGE ROAD | KOLHAPUR | SSS | SANTOSH JADHAV | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
1559 | PUN981 | IDMH107686 | DG | ID_PUNENORTH | 566595 | HOTEL SAFARI_BAUDHAN | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller Faulty | SMPS rectification done | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1560 | NGP215 | IDMH107462 | DG | ID_NAGPUR | 565726 | SHANTI NAGAR, NAGPUR | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1561 | SOLP72 | IDMH108360 | DG | ID_SOLAPUR | 523503 | SOLAPUR ZONAL OFFICE VODAFONE | SOLAPUR | PTPL | SATYASHIL PATIL | SMPS | Controller faulty | SMPS replaced | Closed | 2025-03-23 | 0.5 |  | 0.5 |  | 2
1562 | PUN270 | IDMH107935 | DG | ID_PUNESOUTH | 464929 | BANER CAPACITY | PUNE-2 | ATS | VIPIN GUPTA | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
1563 | SOLP93 | IDMH110459 | DG | ID_SOLAPUR | 565765 | SAINATH NAGAR, BHAGYODAY SOCIETY | SOLAPUR | PTPL | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1564 | BTBR05 | IDMH110206 | NON DG | ID_NAGPUR | 451520 | INDORAMA_VF | NAGPUR | SAI | VIVEK GANJARE | SMPS | SMPS Obsolute model/Single LVD PP | New SMPS Req | Open | 2025-05-30 | 0.5 |  |  | 1 | 2
1565 | ALBG40 | IDMH110470 | DG | ID_RAIGARH | 505445 | GOTEGHAR | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
1566 | PAJ151 | IDMH107024 | NON DG | ID_GOA | 461362 | HOTEL AVNI | GOA | SSS | SURAJ PATIL | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-12 | 1 |  | 0.5 |  | 2
1567 | CHKN68 | IDMH110597 | NON DG | ID_PUNENORTH | 465440 | STAR ENGINEER | PUNE-3 | ATS | PRATIK HULAVALE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1568 | TAKI01 | IDMH111754 | DG | ID_KOLHAPUR | 459721 | TAKALI | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 1.5 |  |  | 2
1569 | PUN744 | IDMH105454 | NON DG | ID_PUNENORTH | 459157 | SAI RADHE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectifiction | Open | 2025-05-22 | 0.5 |  |  |  | 1
1570 | PU1409 | IDMH110626 | DG | ID_PUNENORTH | 500986 | PIMPLE SAUDAGAR-2 | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
1571 | SLWN01 | IDMH110444 | NON DG | ID_NASHIK | 465621 | SULA WINE JAULKE | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1572 | PUNI02 | IDMH110632 | DG | ID_CHANDRAPUR | 531539 | PAUNI 2 | NAGPUR | SAI | SWAPNASHIL CHAVHAN | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-04-09 | 0.5 | 0.5 |  | 2 | 3
1573 | GOND22 | IDMH110629 | DG | ID_CHANDRAPUR | 522681 | MURRI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | I2PMS BER on site | New SMPS Req | Open | 2025-05-15 | 6.5 | 7.5 |  |  | 2
1574 | DAMR01 | IDMH105459 | DG | ID_PUNENORTH | 459606 | DHAMARI | PUNE-1 | SAI | HARSHAL MAHAJAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1575 | PRTR03 | IDMH110639 | DG | ID_AURANGABAD | 505149 | PARTUR | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | SMPS | SMPS LVD card and back plane faulty | Plan for rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1576 | PUNE45 | IDMH105501 | DG | ID_PUNENORTH | 459348 | SHAWAS SOCIETY | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectifiction | Open | 2025-04-20 | 0.5 | 0.5 | 0.5 |  | 3
1577 | JLGN42 | IDMH110693 | DG | ID_AKOLA | 565590 | HANUMAN MANDHIR,RAMPETH | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 1.5 | 3.5 | 1.5 | 2 | 4
1578 | BRGW01 | IDMH108794 | DG | ID_NAGPUR | 525149 | BORI-(GHIWARI)_NEW | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1579 | DULE28 | IDMH111883 | DG | ID_NASHIK | 566393 | DHU 31 JAI SHANKAR COLONYÂ | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 | 1 | 2
1580 | BHAN22 | IDMH110749 | NON DG | ID_CHANDRAPUR | 567164 | PANDE MAHAL, BHANDARA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS BER | SMPS replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1581 | PUN952 | IDMH108317 | DG | ID_PUNESOUTH | 522088 | BANER HILL TOP (IMC) | PUNE-2 | ATS | VIPIN GUPTA | BB | BB Backup very low | BB upgradation done | Closed | 2025-04-24 |  |  | 2 | 2 | 2
1582 | NGP429 | IDMH110754 | DG | ID_NAGPUR | 565462 | MOKSHDHAM | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1583 | ROHA04 | IDMH111908 | NON DG | ID_RAIGARH | 459465 | BHUWANESHWAR | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS BER | SMPS replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1584 | PUN456 | IDMH108803 | NON DG | ID_PUNENORTH | 524525 | OLD SANGHVI 2 | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-30 | 2 |  |  |  | 1
1585 | AURN25 | IDMH111143 | DG | ID_AURANGABAD | 465645 | RELOCATION OF AURN25_USMANPURA | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1586 | NGP124 | IDMH111306 | DG | ID_NAGPUR | 458383 | JAI BHIM CHOWK | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1587 | TPNG01 | IDMH111365 | DG | ID_NANDED | 460360 | TADPANGRI | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 | 1 | 1.5 |  |  | 2
1588 | BHWN01 | IDMH111934 | DG | ID_PUNESOUTH | 459739 | BHIGWAN_BHWN01 | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 | 0.5 |  | 3
1589 | PU2031 | IDMH109206 | DG | ID_PUNENORTH | 566742 | SANGVI2 | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1590 | MHYC01 | IDMH110855 | DG | ID_AURANGABAD | 531310 | ENGG COLLEGE_JALNA | CH SAMBHAJI NAGAR | PTPL | SHIVAJI KANHERE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1591 | PAJ285 | IDMH107878 | NON DG | ID_GOA | 461368 | CONVENTION HOTEL | GOA | SSS | SURAJ PATIL | SMPS | LVD Card faulty . TT No 230305CM1462054 | SMPS rectification done | Closed | 2025-04-24 |  | 1 |  |  | 1
1592 | JLGN40 | IDMH111571 | DG | ID_AKOLA | 566328 | NAHATHA HOSPITAL,BHASKAR MARKRET RD. | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1593 | HNGN01 | IDMH111997 | DG | ID_KOLHAPUR | 459647 | HINGANGAON | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | Smps Controller And Lvd Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1594 | WGPR01 | IDMH107267 | DG | ID_PUNESOUTH | 459568 | WAGHAPUR | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 0.5 |  | 1
1595 | PU1301 | IDMH110888 | DG | ID_PUNESOUTH | 521290 | MAHALUNGE_A | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
1596 | BHAN18 | IDMH110898 | NON DG | ID_CHANDRAPUR | 567162 | APNA NAGAR | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 1 |  |  | 2
1597 | PU1317 | IDMH110912 | NON DG | ID_PUNESOUTH | 465516 | NANDED CITY (MADHUWANTI) | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS Faulty | Plan for SMPS replacement | Open | 2025-05-30 |  |  | 1.5 |  | 1
1598 | PUN936 | IDMH112042 | NON DG | ID_PUNESOUTH | 459236 | DTC-CUMMINS | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS controller faulty | Plan for SMPS replacement | Open | 2025-05-30 |  | 1 |  |  | 1
1599 | PU1119 | IDMH109348 | DG | ID_PUNESOUTH | 566499 | ANUTEJ SYMPHONY | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 |  | 1
1600 | YAVT23 | IDMH112070 | NON DG | ID_AMRAVATI | 565953 | TARANGINI BLDG YAVATMAL | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS LVD Faulty | Plan for SMPS Rectification | Open | 2025-04-20 | 2 | 5 | 1.5 |  | 3
1601 | YAVT22 | IDMH112093 | DG | ID_AMRAVATI | 531393 | PIMPLE GAON | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | Smps Controller Faulty | SMPS rectification done | Closed | 2025-04-24 | 1 | 0.5 |  |  | 2
1602 | PU1162 | IDMH110113 | NON DG | ID_PUNENORTH | 526912 | SHANTINIKETAN SOC - VISHAL NAGAR | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-15 | 1 | 2 |  | 2 | 3
1603 | PU1132 | IDMH110189 | DG | ID_PUNESOUTH | 532975 | DHANKAWADI ANNEXX | PUNE-2 | ATS | RAHUL TUPARE | SMPS | SMPS BER | BER SMPS to replace | Open | 2025-05-30 | 1 |  |  |  | 1
1604 | CHIP11 | IDMH108550 | DG | ID_KOLHAPUR | 565278 | OPEN PLOT CHIPLUN | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 2 |  |  | 1
1605 | PU1270 | IDMH108809 | NON DG | ID_PUNESOUTH | 573807 | HINGANE MALA | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 | 1 | 1 |  | 3
1606 | SELU04 | IDMH110873 | NON DG | ID_NANDED | 465704 | BANSILAL NAGAR | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | Cable replaced | Closed | 2025-02-28 | 1 | 0.5 |  |  | 2
1607 | PUN459 | IDMH107021 | DG | ID_PUNESOUTH | 464928 | MANIKBAUG | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 3 | 1
1608 | PUNE66 | IDMH110659 | NON DG | ID_PUNENORTH | 464755 | MAGARPATTA TOWER2 | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1609 | PLDO01 | IDMH103861 | DG | ID_PUNESOUTH | 458626 | PALASDEO | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan For Smps Rectification | Open | 2025-05-07 | 4 | 1.5 | 3.5 |  | 3
1610 | WORA08 | IDMH112175 | NON DG | ID_CHANDRAPUR | 458420 | GMR_WARORA_COW | NAGPUR | SAI | GANESH DANDALWAR | SMPS | SMPS controller and LVD card faulty | Complaint raised, SMPS replacement required | Open | 2025-05-30 |  | 0.5 |  |  | 1
1611 | PUN836 | IDMH105690 | DG | ID_PUNESOUTH | 500972 | MOHAMADWADI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1 | 1 |  |  | 2
1612 | KTHR01 | IDMH111237 | DG | ID_CHANDRAPUR | 459893 | KOTHARI | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  | 1 | 0.5 |  | 2
1613 | PUN699 | IDMH111768 | NON DG | ID_PUNENORTH | 502949 | RAKSHAK SOCIETY-WAKAD | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
1614 | SHAN01 | IDMH111338 | DG | ID_CHANDRAPUR | 505458 | SHANKARPUR | NAGPUR | SAI | BEERENDRA SINGH | BB | 15 Min Backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1615 | PLGN02 | IDMH111342 | DG | ID_NAGPUR | 505511 | ITI COLLEGE | NAGPUR | SAI | VIVEK GANJARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1616 | NGRI01 | IDMH111382 | DG | ID_CHANDRAPUR | 451349 | NAGARI_V_USO | NAGPUR | SAI | VIVEK GANJARE | RRU | 1 RRU Faulty | RRU replaced | Closed | 2025-02-28 | 0.5 | 0.5 |  | 1 | 3
1617 | BOKR03 | IDMH110784 | DG | ID_NANDED | 505536 | BHOKAR 2 | LATUR | PTPL | RAJKUMAR ALANE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-31 | 2 | 1 | 2 | 3 | 4
1618 | AUR188 | IDMH110892 | DG | ID_AURANGABAD | 565541 | WADGAON KOLHATI | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | LVD Bypass,1 LVD SMPS | SMPS rectification done | Closed | 2025-02-13 | 1 |  |  |  | 1
1619 | GNKD06 | IDMH112253 | NON DG | ID_NANDED | 465656 | POLIC STATION CHOWK | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1620 | HAND01 | IDMH111411 | DG | ID_SOLAPUR | 459306 | HANDARGULI | LATUR | SAI | SUDHIR AGHE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 | 1 | 2
1621 | MDLI01 | IDMH111416 | DG | ID_CHANDRAPUR | 451420 | MADHELI/PANZURNI | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
1622 | WRDH15 | IDMH111441 | DG | ID_NAGPUR | 503550 | NEAR S T DEPOT WARDHA | NAGPUR | SAI | VIVEK GANJARE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1623 | DGHI01 | IDMH105718 | DG | ID_PUNENORTH | 458750 | DIGHI | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-10 | 0.5 | 1.5 | 0.5 |  | 3
1624 | NGPR05 | IDMH111460 | DG | ID_NAGPUR | 565421 | SUKHWANTI, PRATAP NAGAR/JP CHA | NAGPUR | SAI | KAILASH POKALE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 1 | 3.5 | 0.5 | 2 | 4
1625 | NEAJ01 | IDMH110715 | DG | ID_KOLHAPUR | 528925 | NEJ | KOLHAPUR | SSS | SANTOSH JADHAV | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1626 | OZAR01 | IDMH105747 | DG | ID_RAIGARH | 460283 | OZAR | PUNE-1 | ATS | SWAPNIL KARAD | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1627 | ALDI38 | INMH405542 | DG | ID_PUNENORTH | 590973 | Krishna Icon Road | PUNE-1 | ATS | VIJAY KOLI | BB | Low Battery Backup | BB replaced | Closed | 2025-04-24 | 0.5 | 1.5 | 1 | 2 | 4
1628 | PUN359 | IDMH112387 | DG | ID_PUNESOUTH | 566904 | KATRAJ KONDWA RD. | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 1.5 | 2 | 2
1629 | MHKR04 | IDMH111192 | NON DG | ID_AKOLA | 531529 | MEHKAR 3 | AKOLA | SAI | RANJEET KAPSE | SMPS | LVD faulty | SMPS rectification done | Closed | 2025-01-30 | 2 |  |  |  | 1
1630 | URJW01 | IDMH109113 | DG | ID_CHANDRAPUR | 507076 | TALADI ( URJAGRAM ) | NAGPUR | SAI | GANESH DANDALWAR | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
1631 | JLGN16 | IDMH111563 | DG | ID_AKOLA | 503481 | SAHKARI AYODHYA NAGAR | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
1632 | HINJ47 | IDMH112394 | NON DG | ID_PUNESOUTH | 459049 | TECH MAHINDRA PHASE3 S1 BLOCK | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1633 | UMRJ01 | IDMH105884 | DG | ID_RAIGARH | 460277 | UMRAJ | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB cell faulty | BB cell replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1634 | NGPR66 | IDMH112423 | NON DG | ID_NAGPUR | 458342 | RAMDES PETH | NAGPUR | SAI | KAILASH POKALE | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-05-22 |  | 0.5 |  | 1 | 2
1635 | SIRD03 | IDMH111615 | DG | ID_AHMEDNAGAR | 505507 | BHAKTA NIWAS- SHIRDI | AHMEDNAGAR | PTPL | SANDEEP WANI | BB | BB cell faulty | Plan for BB upgradation | Open | 2025-04-30 | 1.5 | 0.5 | 0.5 |  | 3
1636 | JLGN39 | IDMH112307 | DG | ID_AKOLA | 522529 | BIRLA NAGAR,WAGH NAGA,JALGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-20 |  | 0.5 | 0.5 |  | 2
1637 | KLVN03 | INMH002439 | DG | ID_NASHIK | 566519 | KALVAN | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | LVD Faulty | SMPS Rectification Require,LVD Setting 44 to 45 Done | Open | 2025-04-30 |  | 0.5 |  |  | 1
1638 | KNWD01 | IDMH111653 | DG | ID_AHMEDNAGAR | 464757 | KOKANEWADI | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-10 | 0.5 |  |  |  | 1
1639 | KEJJ04 | IDMH112581 | DG | ID_AHMEDNAGAR | 566145 | KAIJ OLD CITY | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 1 |  |  |  | 1
1640 | BHVD01 | IDMH105913 | DG | ID_PUNESOUTH | 459562 | BHIVADI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1641 | CSKN01 | IDMH106277 | DG | ID_PUNENORTH | 460018 | CHAS KAMAN | PUNE-1 | ATS | SWAPNIL KARAD | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1642 | YAVL02 | IDMH112325 | DG | ID_AKOLA | 522693 | YAWAL_B | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-04-09 | 0.5 | 2 | 0.5 | 1 | 4
1643 | KHOP07 | IDMH111706 | DG | ID_RAIGARH | 567872 | JAI DHAM | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1644 | RMWD01 | IDMH111724 | DG | ID_AHMEDNAGAR | 460031 | RAMPURWADI | AHMEDNAGAR | PTPL | SANDEEP WANI | SMPS | SMPS LVD Faulty | SMPS replaced | Closed | 2025-02-13 |  | 0.5 |  |  | 1
1645 | PUN214 | IDMH111747 | DG | ID_PUNENORTH | 458778 | PREMLOK PARK | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1646 | PHTN01 | IDMH100881 | NON DG | ID_PUNESOUTH | 465811 | PATETHAN | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 |  | 2 | 1.5 | 5 | 3
1647 | PU1823 | INMH000974 | DG | ID_PUNESOUTH | 451273 | PADMAKAR_SOCIETY_VF | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-04-09 | 0.5 |  |  | 1 | 2
1648 | TRKD01 | IDMH111788 | DG | ID_NASHIK | 505495 | TORKHEDA | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 3.5 |  |  | 1
1649 | NSK120 | IDMH111790 | DG | ID_NASHIK | 459944 | GARWARE POLYSTER | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
1650 | TDSL01 | IDMH111383 | DG | ID_CHANDRAPUR | 451599 | KURI (TADSAWALI) | AKOLA | SAI | DHANRAJ NIBALKAR | SMPS | SMPS BER | Replacement required | Closed | 2025-01-30 | 1 |  |  |  | 1
1651 | SANG77 | INMH405755 | NON DG | ID_KOLHAPUR | 594382 | Madhavnagar | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | Controller faulty | Controller to be replaced | Open | 2025-04-30 | 0.5 |  |  |  | 1
1652 | ATNE01 | IDMH101951 | DG | ID_PUNESOUTH | 459276 | ANTHURNE | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-07 | 2 | 1 | 1 |  | 3
1653 | PRGN01 | IDMH103307 | DG | ID_PUNESOUTH | 459300 | PARGAON | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
1654 | SAGV01 | IDMH103487 | DG | ID_PUNESOUTH | 459273 | SANGVI (BARAMATI) | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 0.5 | 1 | 2
1655 | ALBG05 | IDMH111921 | DG | ID_RAIGARH | 458920 | CHENDHERE | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1656 | PUN666 | IDMH106885 | DG | ID_PUNENORTH | 505510 | PUNAWALE | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1657 | WRWD01 | IDMH103567 | DG | ID_PUNESOUTH | 505178 | WARWAND | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1658 | SWLI01 | IDMH103675 | DG | ID_PUNESOUTH | 565981 | REPEATER 2-SHIROLI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 | 0.5 |  | 0.5 | 1 | 3
1659 | PUN881 | IDMH111947 | DG | ID_PUNESOUTH | 566723 | BUS STAND KOTHRUD | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-20 | 0.5 |  | 0.5 |  | 2
1660 | CHND25 | IDMH111966 | DG | ID_CHANDRAPUR | 567137 | BHIWARPUR WARD | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  | 1 | 2
1661 | BRMT08 | IDMH104278 | NON DG | ID_PUNESOUTH | 458883 | SIDHESWAR GALLI (BARAMATI) | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 3 | 2 | 1.5 | 2 | 4
1662 | HINJ64 | IDMH109895 | NON DG | ID_PUNESOUTH | 526483 | ASPIRIA_HINJEWADI | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1663 | SINR11 | IDMH112094 | DG | ID_NASHIK | 523220 | SINNER - MALEGAON MIDC _A | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 1.5 | 0.5 |  |  | 2
1664 | SHDA06 | IDMH112116 | DG | ID_NASHIK | 522997 | SHAHADA_A | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-02-15 | 0.5 |  |  |  | 1
1665 | DULE32 | IDMH112119 | DG | ID_NASHIK | 566397 | MOHAMADE NAGAR | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  | 1 | 3
1666 | KIHL01 | IDMH112144 | NON DG | ID_NAGPUR | 458146 | KINHALA (IDEAL ENERGY PROJECT LTD,BELA) | NAGPUR | SAI | VIVEK GANJARE | BB | Low Battery backup | BB replaced | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1667 | NGP340 | IDMH112170 | DG | ID_NAGPUR | 522927 | BUTIBORI VILLAGE_A | NAGPUR | SAI | VIVEK GANJARE | Load Segregation | Baseband critical | Critical to non critical | Closed | 2025-03-31 | 0.5 | 0.5 | 1.5 |  | 3
1668 | GHOT04 | INMH405921 | DG | ID_NASHIK | 567000 | GHOTI TOWN | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS Back Plane Faulty | SMPS Replace,LVD Setting 44 to 45 Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1669 | MEKH01 | IDMH104816 | DG | ID_PUNESOUTH | 459278 | MEKHALI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1670 | JLGN58 | INMH002255 | DG | ID_AKOLA | 565589 | SAWARIYA SUBHASH CHOWK | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB cell faulty | Plan for BB upgradation | Open | 2025-04-30 | 5 |  |  | 1 | 2
1671 | PUN153 | IDMH104876 | DG | ID_PUNESOUTH | 459253 | SBI NAGAR (SUKHSAGAR NAGAR) | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 | 1 |  |  |  | 1
1672 | DSGJ02 | IDMH112225 | DG | ID_CHANDRAPUR | 567172 | DESAIGANJ VADSA | NAGPUR | SAI | BEERENDRA SINGH | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-03-31 |  | 0.5 | 1 |  | 2
1673 | SANG40 | IDMH112214 | DG | ID_KOLHAPUR | 566374 | VISHRAMBAG | KOLHAPUR | SSS | VIVEK DESHPANDE | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1674 | PRGT05 | IDMH112231 | NON DG | ID_PUNENORTH | 528764 | NEAR MAHLE FILTERS-PIRANGUTE | PUNE-2 | ATS | AKSHAY SHELAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1675 | PU1938 | INMH001883 | DG | ID_PUNESOUTH | 566498 | BIBWEWADI | PUNE-2 | ATS | RAHUL TUPARE | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1676 | PUN648 | IDMH105190 | DG | ID_PUNESOUTH | 505498 | SAI NAGAR | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-01-08 | 1 |  |  |  | 1
1677 | BRMT28 | IDMH112310 | NON DG | ID_PUNESOUTH | 528855 | SAILY HILL(BARAMATI BHIGWAN ROAD) | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1678 | KOL117 | IDMH112518 | NON DG | ID_KOLHAPUR | 566344 | UCHGAON | KOLHAPUR | SSS | RITESH RANGOLE | BB | Low Battery backup | Plan for BB upgradation | Open | 2025-04-30 | 0.5 |  |  |  | 1
1679 | SNAS05 | IDMH105191 | DG | ID_PUNENORTH | 505529 | SANASWADI | PUNE-1 | ATS | HARSHAL MAHAJAN | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-31 |  | 0.5 | 0.5 |  | 2
1680 | STNA06 | INMH408104 | DG | ID_NASHIK | 566990 | SATANA | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 2.5 |  |  | 2
1681 | SORP01 | IDMH105310 | DG | ID_PUNESOUTH | 459406 | SORTAPWADI | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 1 | 1.5 | 1 | 4
1682 | DGHI04 | IDMH105379 | DG | ID_PUNENORTH | 566910 | DIGHI | PUNE-1 | ATS | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 | 2 | 2
1683 | JLGN46 | IDMH112417 | DG | ID_AKOLA | 577451 | RAYMOND COLONY | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  |  | 0.5 |  | 1
1684 | PUN643 | IDMH105428 | DG | ID_PUNESOUTH | 505505 | NAWAZISH CHK-KONDHWA KHURD | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 1 | 2 | 2
1685 | PU1646 | IDMH112438 | NON DG | ID_PUNENORTH | 566685 | KSB PUMP | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1686 | NGP930 | IDMH112522 | NON DG | ID_NAGPUR | 573557 | CHATRAPATI NAGAR | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-04-30 |  |  | 0.5 |  | 1
1687 | ALDI06 | IDMH105433 | DG | ID_PUNENORTH | 458855 | ALANDI VADGAON ROAD | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1688 | PU1715 | INMH000912 | NON DG | ID_PUNESOUTH | 525596 | CUMMINS 2 BANER NEW | PUNE-2 | INHOUSE | VIPIN GUPTA | RRU | 1-RRU Malfunctiong | RRU rectification done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
1689 | PU1956 | INMH000957 | DG | ID_PUNENORTH | 566636 | PIMPRI CHURCH | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1690 | JLGN60 | INMH001004 | DG | ID_AKOLA | 565300 | B.J MARKET | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS overload | Plan for SMPS upgradation | Open | 2025-04-30 | 0.5 | 0.5 |  |  | 2
1691 | PU1924 | INMH001005 | DG | ID_PUNESOUTH | 566733 | KARVE NAGAR PUNE | PUNE-2 | ATS | AKSHAY SHELAR | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 |  | 1 |  | 2
1692 | AUR228 | INMH001017 | NON DG | ID_AURANGABAD | 575219 | SHIVAJI STATUE-TV CENTER | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | SMPS | SMPS Faulty | Plan for SMPS replacement | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1693 | BATI01 | INMH001057 | DG | ID_SOLAPUR | 451276 | BMITCOLLAGE_VF | SOLAPUR | PTPL | CHANDRAKANT ANGADI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 3 | 1
1694 | PU1713 | INMH406441 |  | ID_PUNESOUTH | 588386 | BALEWADIPHATA_VF_RELOCATION | PUNE-2 | ATS | VIPIN GUPTA | SMPS | RM faulty | RM replaced | Reopen | 2025-03-31 |  |  | 0.5 | 1 | 2
1695 | URLI04 | IDMH109369 | NON DG | ID_PUNESOUTH | 459397 | FLEETGAURD(NANDUR) | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | Back Panel Faulty Controller Faulty And Fan Faulty | Plan for rectification | Open | 2025-05-22 |  | 0.5 |  |  | 1
1696 | GDCR03 | INMH004786 | DG | ID_CHANDRAPUR | 505306 | MANIKGARH | NAGPUR | SAI | GANESH DANDALWAR | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1697 | PKRI01 | INMH001303 | DG | ID_RAIGARH | 527679 | GOHE | PUNE-1 | ATS | SWAPNIL KARAD | Cable | SMPS to DCDB cable underrated | Cable replacement req | Open | 2025-04-20 | 1 | 0.5 |  |  | 2
1698 | THUR01 | IDMH105526 | DG | ID_PUNESOUTH | 459351 | THEUR | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 |  |  | 0.5 |  | 1
1699 | PUN150 | IDMH109815 | NON DG | ID_PUNESOUTH | 459411 | PHURSUNGI_PUN150 | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectifiction | Open | 2025-05-22 | 0.5 |  |  |  | 1
1700 | PUN597 | IDMH105567 | DG | ID_PUNENORTH | 505119 | KESHAV NAGAR-2 | PUNE-1 | ATS | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1701 | PURN04 | INMH005284 | DG | ID_NANDED | 507035 | PURNA | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | BB | BB Backup very low | BB upgradation done | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1702 | NTPR01 | IDMH102201 | DG | ID_AURANGABAD | 460384 | NATHAPUR | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
1703 | BKTI01 | INMH005304 | DG | ID_CHANDRAPUR | 523936 | BAKTI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
1704 | SELU06 | INMH005279 | NON DG | ID_NANDED | 505094 | SELU | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | SMPS | PP BER | New SMPS Req | Open | 2025-05-30 |  | 0.5 |  |  | 1
1705 | GNPR03 | INMH006107 | DG | ID_AURANGABAD | 507025 | GANGAPUR (GBT) | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | Controller Faulty | Plan for Rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1706 | URLI01 | IDMH105669 | DG | ID_PUNESOUTH | 566567 | M G COLLEGE_URLIKANCHAN | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
1707 | PALI03 | INMH001911 | DG | ID_RAIGARH | 505203 | PALI | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1708 | PU2145 | INMH001970 | NON DG | ID_PUNESOUTH | 451294 | ITIROAD_ENT_VF | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS controller faulty | AMF rectification done | Closed | 2025-02-25 | 1 | 0.5 |  |  | 2
1709 | SHKD02 | INMH002253 | DG | ID_NASHIK | 505101 | SHINDKHEDA | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-03-31 | 0.5 |  | 1.5 |  | 2
1710 | LMBOJ1942-BHADGAON-JAL-VIOM-T | INMH002280 | DG | ID_AURANGABAD | 565537 | BHADGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 1 |  |  |  | 1
1711 | LATR53 | INMH006287 | DG | ID_SOLAPUR | 566166 | SAI HOSPITAL | LATUR | PTPL | SUDHIR AGHE | RRU | VIL RRU faulty | RRU replace | Closed | 2025-03-10 |  | 0.5 |  |  | 1
1712 | BHWL32 | INMH002288 | DG | ID_AKOLA | 505221 | BHUSAVAL WORKSHOP KANDARI | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | DCDB MCB Faulty | MCB Replaced | Closed | 2025-02-28 | 1 | 1 |  |  | 2
1713 | CHKN58 | INMH002292 | NON DG | ID_PUNENORTH | 451295 | GECHAKKAN2_ENT_VF | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 1.5 | 1 | 3
1714 | VRGN04 | INMH0VF552 | NON DG | ID_AKOLA | 529173 | PRATIBHA NAGAR | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB Backup very low | BB replaced | Closed | 2025-03-31 | 2 |  | 0.5 |  | 2
1715 | JMNR06 | INMH002419 | DG | ID_AKOLA | 565750 | JAMNER | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | DCDB MCB Faulty | MCB Replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1716 | NNNI01 | INMH002545 | DG | ID_NASHIK | 458088 | NANDIN RPT | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | SMPS Backplane faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
1717 | NGMN01 | IDMH110566 | DG | ID_PUNENORTH | 465698 | NIMGAON | PUNE-1 | ATS | SWAPNIL KARAD | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 0.5 | 1.5 |  | 1 | 3
1718 | WRDH40 | INMH002831 | NON DG | ID_NAGPUR | 565962 | AREA : WARDH RAILWAY STATION | NAGPUR | INHOUSE | VIVEK GANJARE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1719 | HVRE01 | IDMH110625 | DG | ID_PUNENORTH | 465662 | HIVRE | PUNE-1 | SAI | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 0.5 |  |  | 1
1720 | PUN857 | IDMH107685 | DG | ID_PUNESOUTH | 521937 | TUPE MALA, HADAPSAR | PUNE-1 | ATS | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1721 | PU2006 | IDMH108272 | NON DG | ID_PUNENORTH | 459101 | MAGARPATTA-PENTAGON1 | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 1 | 2
1722 | BKGN01 | IDMH110877 | DG | ID_RAIGARH | 465696 | BHAVADI (KAREGAON) | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS controller faulty | SMPS rectification done | Reopen | 2025-03-31 |  |  | 1 | 2 | 2
1723 | PU2160 | INMH003607 | DG | ID_PUNESOUTH | 566680 | PARIHAR CHOWK_ AUNDH | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
1724 | PU2038 | IDMH109157 | NON DG | ID_PUNENORTH | 575262 | GANESH NAGAR ,BHOPKEL | PUNE-1 | ATS | VIJAY KOLI | Load Segregation | RRU at critical | RRU shifted critical to non critical | Closed | 2025-02-03 | 0.5 | 0.5 |  |  | 2
1725 | PU2404 | INMH404108 | NON DG | ID_PUNENORTH | 587571 | Iiser_Pune_Ibs | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS faulty | SMPS replaced | Closed | 2025-04-24 | 0.5 |  |  |  | 1
1726 | PU2025 | INMH400796 | NON DG | ID_PUNESOUTH | 576785 | RAJIV GANDHI NAGAR | PUNE-2 | ATS | RAHUL TUPARE | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1727 | ASKD01 | IDMH104485 | DG | ID_NASHIK | 458229 | ASKHEDA | NASHIK | ATS | Vacant Vacant CE Nashik | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1728 | PAJ579 | INMH403290 | NON DG | ID_GOA | 582786 | Bits Pilani Admin Building | GOA | SSS | SUNIL TAMSE | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required | 0.5 | 0.5 |  |  | 2
1729 | CHIP17 | INMH404279 | DG | ID_KOLHAPUR | 526077 | CHIPLUN RLY STATION_NEW | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-04-09 | 1 | 2.5 |  | 1 | 3
1730 | PU1139 | IDMH109367 | NON DG | ID_PUNESOUTH | 525771 | ROYAL HEIRTAGE_ DORABJEE MALL | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1731 | PU2023 | IDMH109471 | DG | ID_PUNESOUTH | 574625 | NIRMAL TOWNSHIP | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1732 | PU2037 | IDMH109625 | NON DG | ID_PUNESOUTH | 526305 | GANGA NAGAR JAKAT NAKA. | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1733 | KSTD01 | INMH004765 | DG | ID_CHANDRAPUR | 505273 | KOSONTONDI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-04-09 | 1 |  |  | 1 | 2
1734 | WORA10 | INMH004790 | DG | ID_CHANDRAPUR | 505286 | KAPARA MARKET WARORA | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1735 | AKOT12 | INMH401453 | DG | ID_AKOLA | 566176 | AKOT | AKOLA | SAI | Vacant CE Akola | SMPS | Smps Controller Faulty | Rectification Pending | Open | 2025-04-20 | 1 | 1 |  | 2 | 3
1736 | DGHI10 | IDMH111154 | NON DG | ID_PUNENORTH | 465654 | AIT DIGHI | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-30 |  | 2 |  | 2 | 2
1737 | NWDI01 | IDMH111183 | DG | ID_RAIGARH | 465660 | HOTEL KALASH | PUNE-1 | ATS | SWAPNIL KARAD | BB | Zero Battery Backup | BB replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1738 | ALDI08 | IDMH104122 | DG | ID_PUNENORTH | 458856 | MARKAL - PUNE | PUNE-1 | SAI | VIJAY KOLI | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-31 | 1.5 |  | 0.5 |  | 2
1739 | PU2451 | INMH405220 | DG | ID_PUNESOUTH | 586898 | Supereme Amadore, Baner | PUNE-2 | ATS | VIPIN GUPTA | BB | BB cell Faulty | Cell replaced | Closed | 2025-04-24 | 0.5 | 1 | 0.5 | 1 | 4
1740 | ZDGE01 | IDMH107713 | DG | ID_NASHIK | 458319 | ZODGE | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1741 | PU1224 | IDMH109921 | NON DG | ID_PUNENORTH | 527638 | LAXMI NAGAR, YEWADA | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1742 | CHKN83 | INMH403277 | DG | ID_PUNENORTH | 582900 | Dura Auto Chakan1 | PUNE-1 | ATS | SWAPNIL KARAD | BB | SMPS BER & Zero Backup | SMPS & BB replaced | Closed | 2025-04-24 | 0.5 | 4.5 | 2.5 |  | 3
1743 | CNHL01 | IDMH110095 | DG | ID_PUNENORTH | 525150 | CHINCHOLI_USO | PUNE-1 | ATS | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1744 | PU1732 | INMH006169 | NON DG | ID_PUNESOUTH | 451359 | SHIVNERINAGAR_VF | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS Controller Faulty | SMPS controller rectification Req | Open | 2025-04-20 | 1 |  | 1 | 2 | 3
1745 | PU1077 | IDMH110259 | NON DG | ID_PUNENORTH | 465346 | MAGARPATTA_TWR3_IBS | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  | 0.5 |  | 2
1746 | NGP113 | IDMH111312 | DG | ID_NAGPUR | 505126 | RANI DURGAWATI NAGAR | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1747 | PU1765 | INMH407811 | NON DG | ID_PUNESOUTH | 451364 | AUNDHDMART_VF | PUNE-2 | INHOUSE | VIPIN GUPTA | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-04-24 |  | 0.5 |  |  | 1
1748 | PU2029 | IDMH110392 | NON DG | ID_PUNENORTH | 465293 | TOWER S4 MAGARPATTA CITY | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | Rectifier Back Panel Faulty | Plan for rectification | Open | 2025-05-22 |  |  | 0.5 |  | 1
1749 | AUR396 | INMH405751 | DG | ID_AURANGABAD | 593371 | Prathamesh Nagar | CH SAMBHAJI NAGAR | PTPL | GANESH CHAUDHARI | SMPS | SMPS controller faulty | Rectification Done | Closed | 2025-02-08 | 1.5 | 0.5 |  |  | 2
1750 | EXPH11 | IDMH100371 | DG | ID_RAIGARH | 570262 | MAZGAON TUNNEL KHOPOLI | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1751 | BRSI18 | INMH407441 | DG | ID_SOLAPUR | 565301 | BARSHIP5_2 | SOLAPUR | PTPL | BALASAHEB KADAM | Cable | DCDB to RRU Drop > 3 V | VIL to Replace cable | Open | VIL Support Required |  | 0.5 |  |  | 1
1752 | NSK352 | INMH407853 | NON DG | ID_NASHIK | 451373 | EKLAHAREPOWERSTATION_VF | NASHIK | ATS | SUBHASH SHINDE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 1 |  |  |  | 1
1753 | PU2034 | INMH407877 | NON DG | ID_PUNESOUTH | 528496 | KONDHWA BK | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1754 | MI1076 | IDMH111064 | NON DG | ID_PUNENORTH | 464741 | MAGARPATTA_TWR7_IBS | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1755 | NSK210 | INMH400128 | DG | ID_NASHIK | 567058 | TAJ, AMBAD NASIK | NASHIK | ATS | SUBHASH SHINDE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1756 | PUN388 | IDMH104396 | DG | ID_PUNESOUTH | 459412 | FURSUNGI GAON | PUNE-1 | SAI | VIJAY KOLI | SMPS | Power Plant Controller Faulty | Plan for rectification | Open | 2025-05-15 |  | 0.5 | 0.5 |  | 2
1757 | SOLP55 | IDMH111492 | DG | ID_SOLAPUR | 565785 | NEAR NH9,SARAWADI NAGAR | SOLAPUR | PTPL | SATYASHIL PATIL | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1758 | KOML02 | IDMH112338 | DG | ID_PUNESOUTH | 528504 | DREAMS NIVARA - KOREGAON MUL | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 2 |  |  |  | 1
1759 | PU2200 | INMH000999 | NON DG | ID_PUNENORTH | 565865 | HARIGANGA | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 2.5 |  | 1
1760 | PU2257 | INMH400967 | NON DG | ID_PUNESOUTH | 526850 | PRIDE-NAIKNAVARE ALOMA COUNTRY. | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 |  |  | 0.5 |  | 1
1761 | DADJ01 | IDMH104620 | DG | ID_PUNESOUTH | 458825 | DAUNDAJ | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1762 | PU1960 | INMH001419 | DG | ID_PUNENORTH | 566241 | NAVRANG PLAZA | PUNE-1 | ATS | VIJAY KOLI | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1763 | GOND17 | IDMH111991 | DG | ID_CHANDRAPUR | 567176 | RAMNAGAR | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU faulty | Support req | Open | VIL Support Required | 1 |  |  |  | 1
1764 | NGP581 | INMH402303 | NON DG | ID_NAGPUR | 565448 | NARENDRA NAGAR BRIDGE | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1765 | PUN811 | IDMH104795 | NON DG | ID_PUNESOUTH | 464787 | AMANORA PARK TOWN R5 TOWER | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 |  | 1
1766 | PU2478 | INMH405436 | NON DG | ID_PUNESOUTH | 586773 | Patro Multicuision , Yewealwadi | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-20 |  | 2.5 | 4.5 | 4 | 3
1767 | WDKL02 | INMH405438 | DG | ID_RAIGARH | 591486 | Bori Fata | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1768 | PU1899 | INMH407750 | DG | ID_PUNESOUTH | 566497 | BHARAT JYOTI BUS STOP_BIBEWADI | PUNE-2 | ATS | RAHUL TUPARE | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1769 | PUN286 | INMH403818 | NON DG | ID_PUNESOUTH | 523008 | SHIVANE MIDC ( DUDHANE VASTI SHIVANE) | PUNE-2 | ATS | AKSHAY SHELAR | BB | Battery backup very low | BB replaced | Closed | 2025-04-24 | 1 | 1.5 |  |  | 2
1770 | AMRI01 | INMH403915 | DG | ID_CHANDRAPUR | 583146 | Armori | NAGPUR | SAI | BEERENDRA SINGH | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1771 | CHK136 | INMH405532 | NON DG | ID_PUNENORTH | 587252 | Near Ganesh Mandir, Kurali | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  |  | 2
1772 | JLGN61 | INMHVF1369 | DG | ID_AKOLA | 565595 | HANUMAN MANDHIR,RAMPETH | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | Emerson 2 slot faulty | Plan for Rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
1773 | ALDI24 | INMH405536 | NON DG | ID_PUNENORTH | 589569 | Bloom Residency | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS BER | Controller replaced | Closed | 2025-03-15 | 0.5 |  | 0.5 |  | 2
1774 | DNVT04 | INMH404213 | NON DG | ID_RAIGARH | 584627 | Godrej Boyce Mfg Company_IBS1 | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  |  | 1
1775 | WDNI01 | IDMH102335 | DG | ID_AHMEDNAGAR | 459996 | WADWANI | LATUR | PTPL | ASHWIN KAPSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1776 | TISA01 | INMHVF5259 | DG | ID_KOLHAPUR | 526076 | BIJGHAR_USO | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 | 0.5 | 1 |  |  | 2
1777 | JLGN68 | INMHVF1391 | DG | ID_AKOLA | 566324 | BHUSHAN NAGAR | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-04-30 |  | 1 |  |  | 1
1778 | YAVT07 | INMH404247 | NON DG | ID_AMRAVATI | 458401 | PESHWE COMPLEX | AKOLA | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1779 | HIN129 | INMH404281 | NON DG | ID_PUNESOUTH | 584535 | Tech Mahindra S3_IBS | PUNE-3 | INHOUSE | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 | 0.5 |  | 2
1780 | BHWL35 | INMH404286 | DG | ID_AKOLA | 565753 | BHUSAWAL-2 RAMKRISHNA BUILDING | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 2 |  |  |  | 1
1781 | NSK413 | INMH405562 | DG | ID_NASHIK | 589387 | Airtel_Nasardi river | NASHIK | ATS | MANOJ SINHA | Cable | DCDB to RRU voltage frop > 3 V | Cable replaced | Closed | 2025-01-31 | 1.5 |  |  |  | 1
1782 | PU2225 | INMH408490 | NON DG | ID_PUNENORTH | 566840 | CME DAPODI (DAPODI BRIDGE) | PUNE-2 | ATS | VIPIN GUPTA | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1783 | AUR279 | INMH407695 | DG | ID_AURANGABAD | 566436 | VK MARKET | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1784 | ALDI07 | IDMH104973 | DG | ID_PUNENORTH | 458806 | ALANDI | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS Controller Faulty | SPMS Rectification done | Closed | 2025-01-30 | 1 |  |  |  | 1
1785 | CHKN99 | INMH404539 | DG | ID_PUNENORTH | 585139 | Tetra Park Near | PUNE-3 | ATS | Vacant CE Pune-3 | SMPS | Delta controller faulty | SMPS Rectification done | Closed | 2025-04-24 |  | 0.5 | 1 | 3 | 3
1786 | GANG01 | IDMH102054 | DG | ID_SOLAPUR | 459624 | GANGAPUR | LATUR | SAI | SUDHIR AGHE | Cable | SMPS to BTS cable underrated voltage drop >2.6V | Plan for cable replacement | Open | 2025-04-20 | 0.5 | 1 |  |  | 2
1787 | CHK115 | INMH405737 | DG | ID_PUNENORTH | 566804 | KHARABWADI_CHAKAN | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | Smps Controller Faulty | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 1.5 |  | 1 | 3
1788 | NASK48 | INMH404770 | NON DG | ID_NASHIK | 459931 | KAMATHWADI | NASHIK | NonActive | SUBHASH SHINDE | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1789 | PUN433 | INMH405036 | DG | ID_PUNENORTH | 458811 | MOSHI | PUNE-3 | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1790 | AMBK01 | IDMH101596 | DG | ID_SOLAPUR | 458873 | AMBULGA BK | LATUR | SAI | SUDHIR AGHE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1791 | PU2340 | INMH002337 | NON DG | ID_PUNENORTH | 451297 | SAHYADRIHOSP_KLYNG_VF | PUNE-1 | ATS | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1792 | PUN160 | IDMH112407 | DG | ID_PUNENORTH | 505528 | DANGE CHOWK | PUNE-3 | ATS | Vacant Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 1 |  | 1 | 2
1793 | PU2178 | INMH004674 | DG | ID_PUNESOUTH | 566264 | KONDHWA BK7(IMIL) | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-30 | 0.5 |  |  |  | 1
1794 | CHK109 | INMH405526 | NON DG | ID_PUNENORTH | 589368 | Airtel_Near Vaibhav yashwonth Shingankar | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS LVD Faulty | SMPS rectification done | Closed | 2025-03-31 |  | 1.5 |  |  | 1
1795 | CHK111 | INMH405527 | DG | ID_PUNENORTH | 574930 | RACOLD THERMO LTD. | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-04-20 | 2.5 | 2 | 1.5 |  | 3
1796 | DULE42 | IDMH111104 | NON DG | ID_NASHIK | 529514 | KUMAR NAGAR BETA_NEW | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 | 1 | 4 | 4
1797 | PU2237 | INMH408621 | DG | ID_PUNESOUTH | 521807 | KBL BYPASS BANER | PUNE-2 | ATS | VIPIN GUPTA | RRU | 1-RRU Malfunctiong | RRU rectification done | Closed | 2025-03-31 | 1 | 0.5 | 0.5 |  | 3
1798 | PU2477 | INMH405535 | NON DG | ID_PUNESOUTH | 587477 | Eknathpuram housing soc, Suresh Nagar | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  |  | 1 | 1 | 2
1799 | PU2152 | INMH003173 | NON DG | ID_PUNENORTH | 451305 | IBMYERWADA2_W3G | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  | 0.5 |  | 3 | 2
1800 | PU2718 | INMH405964 | NON DG | ID_PUNENORTH | 588026 | Airtel_Govind Garden, Shinde vasat | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending | 2.5 | 5 |  |  | 2
1801 | NGP722 | INMH406011 | NON DG | ID_NAGPUR | 593876 | Prasad_Nagar_Nagpur | NAGPUR | SAI | KAILASH POKALE | SMPS | SMPS RM Hang | Plan for SMPS rectification | Open | 2025-04-20 | 1.5 | 0.5 | 0.5 |  | 3
1802 | MHKR08 | INMH405757 | NON DG | ID_AKOLA | 594475 | Shiv Swarajya | AKOLA | SAI | RANJEET KAPSE | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-07 | 3 | 1 | 0.5 |  | 3
1803 | KDHR01 | IDMH101533 | DG | ID_NANDED | 459390 | KANDAHAR | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Faulty | SMPS replaced | Closed | 2025-02-15 | 2 |  |  |  | 1
1804 | NGP506 | INMH406175 | NON DG | ID_NAGPUR | 507032 | TALENKHEDI | NAGPUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1805 | NGP652 | INMH405559 | DG | ID_NAGPUR | 565385 | INDIRA GANDHI NAGAR | NAGPUR | SAI | MILIND RAMTEKE | SMPS | Controller Faulty | Plan for rectification | Open | 2025-04-30 |  | 0.5 |  |  | 1
1806 | CHND64 | INMH405560 | NON DG | ID_CHANDRAPUR | 593953 | Babupeth | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1807 | NGP693 | INMH405563 | NON DG | ID_NAGPUR | 593635 | Nagpur_Metropolitan Area | NAGPUR | SAI | MILIND RAMTEKE | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1808 | PU2419 | INMH404234 | DG | ID_PUNENORTH | 587279 | VIL_Admin Building of AFMC | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-31 | 1 | 2 | 1 |  | 3
1809 | MRTA01 | IDMH101432 | DG | ID_NANDED | 459900 | MORTALA | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-23 | 0.5 | 0.5 | 0.5 |  | 3
1810 | AHER01 | INMH000492 | DG | ID_SOLAPUR | 458908 | AHERWADI | SOLAPUR | SAI | SATYASHIL PATIL | SMPS | LVD Faulty | Plan for rectification SMPS | Open | 2025-05-15 | 0.5 | 1 |  |  | 2
1811 | DUND18 | INMH406504 | NON DG | ID_PUNESOUTH | 589232 | Airtel_Gopalwadi | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 0.5 | 1 | 2
1812 | DULE02 | IDMH111595 | NON DG | ID_NASHIK | 503137 | DEVPUR (DULE02RELOCATION) | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 0.5 |  | 1
1813 | SNAS13 | INMH406509 | NON DG | ID_PUNENORTH | 595145 | Koregaon_Bhima | PUNE-1 | ATS | HARSHAL MAHAJAN | BB | BB Backup Very Low | Plan for BB upgradation | Open | 2025-05-30 |  | 1.5 |  |  | 1
1814 | PHND01 | IDMH111769 | DG | ID_GOA | 458966 | PHONDA GHAT | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1815 | HRNI01 | INMH405763 | DG | ID_KOLHAPUR | 459583 | HARNAI | KOLHAPUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1816 | NGP451 | INMH006196 | DG | ID_NAGPUR | 565381 | SHANTI NAGAR-DR.MODI/DR.JESHWANI | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 4 | 1
1817 | PUN205 | IDMH105843 | DG | ID_PUNENORTH | 459180 | GPO PUNE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS Controller Faulty | SMPS controller rectification Req | Open | 2025-04-30 |  |  | 1 |  | 1
1818 | KONN01 | INMH406698 |  | ID_RAIGARH | 586504 | Indiabulls Greens Panvel, Sawala Apta Rd | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS BER | SMPS Rectification Done | Closed | 2025-01-30 | 2 |  |  |  | 1
1819 | BAMH02 | INMH404761 | DG | ID_CHANDRAPUR | 567148 | GURUNANAK PUBLIC SCHOOL | NAGPUR | SAI | GANESH DANDALWAR | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1820 | ARVI06 | INMH405924 | DG | ID_NAGPUR | 565998 | DURGAVATI NAGAR ARVI | NAGPUR | SAI | VIVEK GANJARE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
1821 | PU2210 | INMH407694 | DG | ID_PUNENORTH | 566944 | WADGAONSHERI | PUNE-1 | ATS | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 1 | 2
1822 | AKLT03 | IDMH101608 | NON DG | ID_SOLAPUR | 458902 | AKKALKOT 2 | SOLAPUR | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1823 | PU2180 | INMH005116 | NON DG | ID_PUNENORTH | 579111 | CITY TOWER-1 | PUNE-1 | INHOUSE | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1824 | NGP697 | INMH405765 | NON DG | ID_NAGPUR | 593780 | Sidharth Ngr | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 3 | 2
1825 | ALDI01 | IDMH105863 | DG | ID_PUNENORTH | 464857 | ALANDI | PUNE-1 | SAI | VIJAY KOLI | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1 |  | 1
1826 | SANG07 | INMH406437 | NON DG | ID_KOLHAPUR | 459702 | ASTARATNA,100 FEET ROAD | KOLHAPUR | NonActive | VIVEK DESHPANDE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 | 0.5 |  | 4 | 3
1827 | DULE61 | INMH407745 | DG | ID_NASHIK | 566033 | MUTHA HOSPITAL,NH6 RD. | NASHIK | ATS | SWAPNIL SALWE | SMPS | Smps Controller Faulty | SMPS replaced | Closed | 2025-02-19 |  | 0.5 |  |  | 1
1828 | DNCH05 | INMH406439 | NON DG | ID_NASHIK | 505110 | DONDAICHA | NASHIK | NonActive |  | SMPS | SMPS Obsolute model | Plan for SMPS Replacement | Open | 2025-05-07 | 4.5 | 0.5 | 1 | 1 | 4
1829 | INAM01 | IDMH105927 | DG | ID_PUNESOUTH | 458977 | INAMGAON | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS Controller Faulty | SMPS controller rectification Req | Open | 2025-05-15 | 0.5 | 0.5 |  | 1 | 3
1830 | PUN127 | IDMH106661 | DG | ID_PUNENORTH | 458784 | BIJALI NAGAR | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1831 | SHVN01 | IDMH107841 | DG | ID_PUNESOUTH | 459450 | SHINDWANE | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1832 | JMSD01 | IDMH111824 | DG | ID_GOA | 458964 | JAMSANDE | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS Faulty | Eltek SMPS need to replace | Open | 2025-04-30 | 1.5 | 0.5 |  |  | 2
1833 | CDVL01 | IDMH103573 | DG | ID_NASHIK | 458222 | CHHADVEL | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-15 | 2 |  |  |  | 1
1834 | KUDL03 | IDMH105549 | DG | ID_GOA | 565250 | OPEN PLOT KUDAL | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  |  | 0.5 |  | 1
1835 | PUN890 | IDMH107900 | NON DG | ID_PUNENORTH | 465396 | MATRIX MALL KHARADIV | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS Controller Faulty | SMPS controller rectification Req | Open | 2025-05-07 | 5.5 | 2 | 4 | 8 | 4
1836 | PU2207 | INMH407640 | DG | ID_PUNESOUTH | 572833 | BALEWADI_PARVATI NIWAS | PUNE-2 | ATS | VIPIN GUPTA | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1837 | LOHA03 | IDMH112173 | DG | ID_NANDED | 502800 | LOHA-2 | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 0.5 |  |  | 1 | 2
1838 | LONI08 | INMH407474 | NON DG | ID_AHMEDNAGAR | 451453 | PRAVARAMEDICAL_VF | AHMEDNAGAR | INHOUSE | SANDEEP WANI | BB | BB cell faulty | BB replaced | Closed | 2025-04-24 | 0.5 | 0.5 |  |  | 2
1839 | PU2226 | INMH408497 | NON DG | ID_PUNESOUTH | 451475 | SHIVSAGARNGR_VF | PUNE-2 | ATS | RAHUL TUPARE | SMPS | LVD Faulty | SMPS Rectification Done | Closed | 2025-02-15 | 0.5 |  |  |  | 1
1840 | NAND50 | IDMH108097 | DG | ID_NANDED | 531348 | BASMAT PHATA | LATUR | PTPL | Vacant CE Latur | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 | 2 | 1.5 |  |  | 2
1841 | DGLR05 | INMH408514 | DG | ID_NANDED | 531528 | MAHATMA NAGAR | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS BER | SMPS Rectiications required , NFA received | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1842 | PRLI11 | IDMH110331 | DG | ID_AHMEDNAGAR | 565808 | PARLI VAIJANATH | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS BER | Plan for SMPS Replacement | Open | 2025-05-30 |  | 0.5 |  |  | 1
1843 | DVEA01 | INMH407395 | DG | ID_RAIGARH | 570217 | DIVEAGAR | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS Calliberation issue | SMPS rectification done | Closed | 2025-04-24 | 1.5 |  |  |  | 1
1844 | CHKR03 | IDMH109401 | DG | ID_SOLAPUR | 505087 | CHAKOR | LATUR | PTPL | SUDHIR AGHE | BB | BB Backup low | Plan for BB upgradation | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1845 | RGWN01 | INMH407392 | DG | ID_RAIGARH | 570246 | VILLAGE WAGHOLIWADI / TALAWADE ALIBAUG | PUNE-3 | ATS | ANANT TIDKE | VIL Planned Activity | VIL L900 Activity | NA | Closed | 2025-01-31 | 0.5 |  |  |  | 1
1846 | PU1693 | INMH408477 | NON DG | ID_PUNENORTH | 577411 | ARMY CANTONMENT | PUNE-2 | INHOUSE | VIPIN GUPTA | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1847 | LNVL32 | INMH408544 | NON DG | ID_RAIGARH | 451465 | DEVGIRIHOSTEL_VF | PUNE-3 | ATS | PRATIK HULAVALE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1848 | UMRI01 | IDMH100722 | DG | ID_NANDED | 505206 | PETH UMRI | LATUR | PTPL | RAJKUMAR ALANE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-23 | 0.5 |  | 1.5 |  | 2
1849 | BHMP08 | INMH408481 | DG | ID_CHANDRAPUR | 522527 | SHARDA COLONY | NAGPUR | SAI | BEERENDRA SINGH | RRU | RRU connector faulty | RRU rectification done | Closed | 2025-03-03 | 2 | 0.5 | 0.5 |  | 3
1850 | SOL123 | INMH408444 | NON DG | ID_SOLAPUR | 566249 | NEAR BANDARI HOSPITAL | SOLAPUR | PTPL | SATYASHIL PATIL | SMPS | LVD Faulty | Plan for rectification SMPS | Open | 2025-04-30 |  | 0.5 |  |  | 1
1851 | SAII02 | INMH407437 | NON DG | ID_RAIGARH | 451473 | ARSHIYA_VF | PUNE-3 | ATS | ANANT TIDKE | BB | Low Battery Backup | BB Replacement required | Open | 2025-05-30 | 0.5 |  |  |  | 1
1852 | NAN130 | INMH405724 | DG | ID_NANDED | 575208 | MARKANDAYRUSHI CHOWK | LATUR | PTPL | Vacant CE Latur | BB | Zero Battery Backup | Plan for BB upgradation | Open | 2025-05-07 | 1.5 | 0.5 | 0.5 |  | 3
1853 | WRDH38 | INMH408423 | NON DG | ID_NAGPUR | 576971 | GEETAI NAGAR | NAGPUR | SAI | VIVEK GANJARE | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1854 | NSK380 | INMH408424 | DG | ID_NASHIK | 576976 | LAST BUS STOP | NASHIK | ATS | Vacant Vacant CE Nashik | SMPS | Smps Controller And Lvd Faulty | Plan for SMPS replacement | Open | 2025-05-30 |  | 1 |  |  | 1
1855 | PU1838 | INMH407758 | DG | ID_PUNENORTH | 566879 | INDRAYANI NAGAR (DWARKA PLATINUM) | PUNE-3 | ATS | Vacant CE Pune-3 | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1856 | KTHA01 | IDMH100492 | DG | ID_NANDED | 459556 | KAUTHA | LATUR | PTPL | RAJKUMAR ALANE | RRU | RRU Faulty | RRU replaced | Closed | 2025-03-03 | 0.5 |  | 1 |  | 2
1857 | PU2635 | INMH405538 | NON DG | ID_PUNENORTH | 591743 | Ramnagar_Airtel | PUNE-1 | ATS | HARSHAL MAHAJAN | BB | BB Backup Very Low | BB replaced | Closed | 2025-03-31 | 0.5 |  | 1 |  | 2
1858 | MJRM01 | IDMH102031 | DG | ID_NANDED | 464926 | MANJARAM | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS Obsolute model | Plan for SMPS replacement | Open | 2025-05-07 | 0.5 | 2.5 | 1 |  | 3
1859 | NGP529 | INMH408415 | DG | ID_NAGPUR | 565474 | ULHAS NAGAR | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Obsolute Model | Plan for SMPS replacement | Open | 2025-04-30 |  | 1.5 |  | 1 | 2
1860 | CHML01 | IDMH102786 | DG | ID_AHMEDNAGAR | 458816 | CHINCHOLI MALI | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
1861 | PU1806 | INMH408434 | NON DG | ID_PUNENORTH | 451507 | SRPF2_VF | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS BER | Plan for SMPS Replacement | Open | 2025-05-07 | 0.5 | 3.5 | 1 |  | 3
1862 | BHWL28 | INMHVF3024 | DG | ID_AKOLA | 531578 | TAPI NAGAR_BHUSAWAL | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-03-31 |  | 1 | 1 |  | 2
1863 | MJLG05 | IDMH109242 | DG | ID_AURANGABAD | 565653 | MANJIRATH ROAD,MAJALGAON | LATUR | PTPL | ASHWIN KAPSE | RRU | VIL RRU faulty | RRU replacement req | Open | VIL Support Required | 1 | 0.5 |  |  | 2
1864 | PU2260 | INMH407982 | NON DG | ID_PUNESOUTH | 451534 | AMANORA_TWR15_VF | PUNE-1 | INHOUSE | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 1 |  | 3.5 | 1 | 3
1865 | SNGG01 | INMH407581 | DG | ID_RAIGARH | 570247 | SANEGAON RPTR- | PUNE-2 | ATS | AMAY DORUGADE | RRU | RRU faulty | RRU replacement req | Open | VIL Support Required | 0.5 |  | 0.5 | 2 | 3
1866 | KRPT02 | IDMH109826 | DG | ID_GOA | 566997 | KHAREPATAN | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required | 0.5 |  |  |  | 1
1867 | ALBG45 | INMH407357 | NON DG | ID_RAIGARH | 451550 | RADISSIONBLU_VF | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending | 1 |  |  | 2 | 2
1868 | VNCR01 | IDMH101762 | DG | ID_NASHIK | 458269 | VINCHUR | NASHIK | ATS | SWAPNIL SALWE | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 1 | 2
1869 | VIJE01 | INMHVF4802 | DG | ID_KOLHAPUR | 505376 | BHOOM | KOLHAPUR | SSS | VIVEK GOSAVI | SMPS | Smps Controller Faulty | Rectification Done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1870 | PAJ474 | IDMH110604 | NON DG | ID_GOA | 465435 | SUN VILLAGE ARPORA | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  |  | 1 |  | 1
1871 | DORI03 | INMH407283 | DG | ID_CHANDRAPUR | 567189 | DEORI_OPEN PLOT | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  | 1 |  |  | 1
1872 | PU1925 | INMH408169 | NON DG | ID_PUNENORTH | 576355 | MASKEWASTI | PUNE-1 | ATS | HARSHAL MAHAJAN | SMPS | SMPS controller fauly | Rectification planned | Open | 2025-04-20 | 1 | 2 | 1 | 2 | 4
1873 | PU2338 | INMH408484 | NON DG | ID_PUNENORTH | 451472 | BHARATFORGE_VF | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 | 0.5 |  |  |  | 1
1874 | ARVI05 | INMH406873 | DG | ID_NAGPUR | 565999 | GOVT. HOSPITAL ARVI | NAGPUR | SAI | VIVEK GANJARE | VIL Planned Activity | VIL L2100 Activity | NA | Closed | 2025-02-28 | 0.5 | 0.5 |  |  | 2
1875 | CHRT01 | IDMH112168 | DG | ID_GOA | 531336 | KARIWADE | GOA | SSS | KISHOR SHIRSATH | SMPS | SMPS Controller faulty SR NO 23R210202N04801970 TT NO 250130CM3015864 | SMPS Rectification done | Closed | 2025-03-31 | 0.5 |  |  |  | 1
1876 | KRJN02 | INMH408138 | DG | ID_AMRAVATI | 505341 | KARANJA | AKOLA | SAI | ALI SHAH | SMPS | smps faulty | SMPS replaced | Closed | 2025-04-24 | 0.5 | 2.5 | 0.5 | 7 | 4
1877 | GOND32 | INMH407153 | NON DG | ID_CHANDRAPUR | 451565 | BAJAJNAGAR2_GON_VF | NAGPUR | SAI | SWAPNASHIL CHAVHAN | RRU | RRU faulty | Support req | Open | VIL Support Required | 1.5 |  |  | 4 | 2
1878 | PU1670 | INMH408214 | DG | ID_PUNESOUTH | 566286 | PHURSUNGI | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-04-30 | 1 |  |  |  | 1
1879 | RTLI01 | IDMH101064 | DG | ID_NANDED | 464909 | RATOLI | LATUR | PTPL | RAJKUMAR ALANE | Load Segregation | RRU at Critical | Load segregation done | Closed | 2025-04-09 | 0.5 | 1 | 0.5 | 1 | 4
1880 | PAJ369 | INMH003312 | NON DG | ID_GOA | 451306 | BAGAMARINE_VF | GOA | SSS | KISHOR SHIRSATH | RRU | RRU cable faulty | Cable replacement req | Open | VIL Support Required |  | 0.5 |  |  | 1
1881 | PU2297 | INMH408133 | NON DG | ID_PUNENORTH | 532353 | I SPACE (KOLTE PATIL) | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Back panal faulty | SMPS rectification done | Closed | 2025-03-16 |  | 1 | 0.5 |  | 2
1882 | NAND56 | IDMH112186 | NON DG | ID_NANDED | 526241 | BORBAN FACTORY AREA. | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1883 | DGON01 | IDMH104950 | DG | ID_NASHIK | 457963 | DEAGAON | NASHIK | ATS | NILESH BHAVSAR | BB | Zero Battery Backup | BB replaced | Closed | 2025-02-17 | 0.5 | 0.5 |  |  | 2
1884 | ALBG47 | INMH407312 | NON DG | ID_RAIGARH | 531141 | ALIBAG GBT | PUNE-3 | ATS | ANANT TIDKE | Update pending | Update pending | Update pending | Update pending | Update pending | 1 | 0.5 | 0.5 |  | 3
1885 | PU2307 | INMH408276 | NON DG | ID_PUNESOUTH | 451572 | NSGHOTEL_VF | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-04-24 |  |  | 1 |  | 1
1886 | HDGN01 | IDMH100225 | DG | ID_NANDED | 459831 | HADGAON | LATUR | PTPL | RAJKUMAR ALANE | RRU | VIL RRU faulty | RRU replaced | Closed | 2025-03-10 |  | 1.5 |  |  | 1
1887 | DIVE03 | INMH407980 | NON DG | ID_PUNESOUTH | 451535 | JADHAVGADH_VF | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectifiction | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1888 | PU1873 | INMH407977 | DG | ID_PUNESOUTH | 565867 | KONDHWA GAONTHAN PUNE | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 | 0.5 |  |  |  | 1
1889 | NGP591 | INMH408311 | DG | ID_NAGPUR | 451574 | SBJAINCOLLEGE_VF | NAGPUR | SAI | LEELADHAR BHOSKAR | BB | Low Battery Backup | Plan for BB upgradation | Open | 2025-05-15 | 1 |  | 2.5 | 1 | 3
1890 | MTSS01 | INMHVF6141 | DG | ID_SATARA | 525092 | NIPRO | PUNE-2 | ATS | RAHUL TUPARE | RRU | RRU faulty | RRU replaced | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1891 | KHDP01 | INMH407216 | DG | ID_CHANDRAPUR | 523944 | KHADIPAR | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS Controller fault | SMPS Rectification planeed | Open | 2025-04-30 |  |  | 1 |  | 1
1892 | SKLI05 | INMH407292 | DG | ID_CHANDRAPUR | 567174 | SAKOLI 2 | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS Controller faulty | SMPS rectification done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1893 | PRGT10 | INMH406495 | NON-DG | ID_PUNENORTH | 586770 | Punnyai Building,Pirangut Camp | PUNE-2 | ATS | AKSHAY SHELAR | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-07 | 1 | 3 | 1 | 4 | 4
1894 | GVRI06 | INMH408646 | DG | ID_AHMEDNAGAR | 591949 | Georai | LATUR | PTPL | ASHWIN KAPSE | SMPS | SMPS BER | SMPS Rectified & BB Replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1895 | UMRI02 | IDMH110536 | DG | ID_NANDED | 565840 | UMRI T RLY | LATUR | PTPL | RAJKUMAR ALANE | SMPS | SMPS Controller and RM slot | SMPS rectification done | Closed | 2025-04-24 | 0.5 | 1 |  |  | 2
1896 | NASK32 | IDMH106629 | NON DG | ID_NASHIK | 459960 | MUMBAI NAKA | NASHIK | ATS | SUBHASH SHINDE | Cable | Underrated Cable Voltage Drop 6 Volt, | LVD Setting44 to 45 Correction Done & VIL to replace cable | Open | VIL Support Required | 1 |  |  |  | 1
1897 | SHDA07 | IDMH112087 | DG | ID_NASHIK | 531325 | MALONI VILLAGE | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-02-15 | 2 |  |  |  | 1
1898 | CHDI01 | IDMH102454 | DG | ID_AHMEDNAGAR | 507117 | CHINCHWADI(CHICHONDI) | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-03-10 | 1.5 | 2.5 |  |  | 2
1899 | NGPR52 | IDMH100252 | DG | ID_NAGPUR | 458374 | HUDKESHWAR ROAD | NAGPUR | SAI | MILIND RAMTEKE | SMPS | SMPS Faulty | SMPS replaced | Reopen | 2025-01-30 | 1 |  |  | 7 | 2
1900 | PNVL07 | IDMH105578 | DG | ID_RAIGARH | 459387 | GUSALWADI | PUNE-3 | ATS | ANANT TIDKE | BB | BB Backup Zero | Plan for BB upgradation | Open | 2025-05-15 | 5.5 | 0.5 |  |  | 2
1901 | PUN554 | IDMH111892 | DG | ID_PUNESOUTH | 459258 | MIT COLLEGE | PUNE-2 | ATS | AKSHAY SHELAR | BB | Battery backup very low | Plan for BB upgradation | Open | 2025-05-15 | 1 |  | 1.5 | 2 | 3
1902 | NGP321 | IDMH109901 | DG | ID_NAGPUR | 565406 | PADAVAL LAYOUT | NAGPUR | SAI | KAILASH POKALE | BB | Low Battery Backup | BB replaced | Reopen | 2025-03-31 | 1.5 | 0.5 | 0.5 | 1 | 4
1903 | JWRI01 | IDMH103790 | DG | ID_CHANDRAPUR | 465827 | JAWARI | NAGPUR | SAI | SWAPNASHIL CHAVHAN | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-22 |  |  | 0.5 | 3 | 2
1904 | NVPR01 | IDMH106377 | DG | ID_NASHIK | 458017 | NAVAPUR | NASHIK | ATS | NILESH BHAVSAR | SMPS | LVD Faulty | Plan for SMPS replacement | Open | 2025-05-07 | 0.5 | 0.5 | 0.5 |  | 3
1905 | PNST14 | INMH001846 | DG | ID_PUNESOUTH | 566227 | KHOPI | PUNE-2 | ATS | RAHUL TUPARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 4 | 1
1906 | TLGN55 | INMH405541 | DG | ID_RAIGARH | 590310 | Swapna Nagari | PUNE-3 | ATS | PRATIK HULAVALE | SMPS | SMPS controller faulty | SMPS replaced | Closed | 2025-04-24 | 2.5 | 1 | 0.5 |  | 3
1907 | PLTN02 | IDMH103366 | DG | ID_SATARA | 566593 | MODI COMPLEX | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1908 | MORN01 | IDMH109561 | DG | ID_NASHIK | 525901 | MOGRANI_USO | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  | 1.5 |  | 1
1909 | WRDH14 | IDMH101283 | DG | ID_NAGPUR | 565961 | SAI NAGAR CHOUK - WARDHA | NAGPUR | SAI | VIVEK GANJARE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1910 | PAJ317 | IDMH107123 | DG | ID_GOA | 565893 | AMBAJI ROAD | GOA | SSS | SUNIL TAMSE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1911 | NGP422 | IDMH110421 | NON DG | ID_NAGPUR | 576789 | DHANTOLI | NAGPUR | SAI | LEELADHAR BHOSKAR | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 1 | 1
1912 | NAND36 | IDMH111474 | DG | ID_NANDED | 565684 | DEGLOOR NAKA | LATUR | PTPL | Vacant CE Latur | SMPS | SMPS Controller Faulty | SMPS replaced | Closed | 2025-04-24 | 4 | 0.5 |  |  | 2
1913 | KKNA01 | IDMH101880 | NON DG | ID_AHMEDNAGAR | 460013 | KUKANA | AHMEDNAGAR | PTPL | DNYANESHWAR POTHARE | BB | BB Backup very low | Plan for BB upgradation | Open | 2025-05-15 |  | 0.5 | 0.5 |  | 2
1914 | YAVL01 | IDMH102469 | DG | ID_AKOLA | 457961 | YAVAL | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | Delta LLVD fault | Plan for rectification | Open | 2025-04-20 |  | 1.5 | 3 | 2 | 3
1915 | KRJT01 | IDMH105544 | DG | ID_RAIGARH | 464766 | KARJAT (RL) | PUNE-3 | ATS | ANANT TIDKE | SMPS | SMPS controller faulty | SMPS rectification done | Closed | 2025-04-24 | 1 | 1 | 0.5 | 1 | 4
1916 | GOND31 | INMH000373 | NON DG | ID_CHANDRAPUR | 576973 | GONDIA | NAGPUR | INHOUSE | SWAPNASHIL CHAVHAN | SMPS | SMPS Controller fault | SMPS Rectification planeed | Open | 2025-05-07 | 5 | 5 | 11.5 | 13 | 4
1917 | PAJ235 | IDMH105737 | NON DG | ID_GOA | 461357 | BASTORA | GOA | SSS | KISHOR SHIRSATH | Cable | Voltage drop | VIL need to replace and need to shift SMPS+OD Cabinet at top floor of 5th Floor building | Open | VIL Support Required | 1 |  |  |  | 1
1918 | KTBD01 | IDMH103221 | DG | ID_AURANGABAD | 505091 | KHULTABAD SHLUBHANJAN | CH SAMBHAJI NAGAR | PTPL | CHANDRASHEKHAR MORTULE | RRU | VIL RRU Faulty | RRU Replacement done | Closed | 2025-02-28 |  | 1 |  |  | 1
1919 | PUN339 | IDMH105394 | DG | ID_PUNESOUTH | 464851 | MAHADEV NAGAR | PUNE-1 | SAI | VIJAY KOLI | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-04-30 |  | 0.5 |  | 1 | 2
1920 | BHER01 | IDMH108149 | DG | ID_NASHIK | 566633 | BAMER | NASHIK | ATS | NILESH BHAVSAR | Update pending | Update pending | Update pending | Update pending | Update pending |  | 0.5 |  |  | 1
1921 | PUN781 | IDMH104580 | DG | ID_PUNESOUTH | 464784 | KALEPADAL | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  |  | 1
1922 | PUN251 | IDMH106415 | NON DG | ID_PUNESOUTH | 459182 | PERSISTENT,ERANDAWANE | PUNE-2 | ATS | AKSHAY SHELAR | Load Segregation | VIL equipment at critical | Dual supply disconnect from BB & Critical to non critical connection done | Reopen | 2025-03-31 | 0.5 |  | 1 | 2 | 3
1923 | BOND01 | IDMH103780 | DG | ID_SATARA | 459681 | BONDLE | SOLAPUR | SAI | CHANDRAKANT ANGADI | BB | BB Backup very low | BB replaced | Closed | 2025-01-30 | 0.5 |  |  |  | 1
1924 | RNGI01 | IDMH100245 | DG | ID_CHANDRAPUR | 451432 | RANGI | NAGPUR | SAI | BEERENDRA SINGH | SMPS | SMPS Controller faulty | Controller replaced | Closed | 2025-04-09 |  |  | 2 | 2 | 2
1925 | PU1265 | IDMH108573 | NON DG | ID_PUNENORTH | 526897 | LAXMI SOC - VISHRANTWADI | PUNE-1 | ATS | VIJAY KOLI | SMPS | SMPS LVD Faulty | Plan For Smps Rectification | Open | 2025-05-07 | 5 | 0.5 | 1.5 |  | 3
1926 | HING10 | IDMH110258 | DG | ID_NAGPUR | 523517 | FRIDAY MARKET | NAGPUR | SAI | VIVEK GANJARE | SMPS | Power Plant Faulty | Plan for rectification | Open | 2025-04-30 | 1.5 |  |  | 1 | 2
1927 | MNDY01 | IDMH109011 | DG | ID_NASHIK | 525938 | MANMODYA_USO | NASHIK | ATS | NILESH BHAVSAR | SMPS | RM Bypass | Plan for rectification' | Open | 2025-05-15 |  | 1 | 6 |  | 2
1928 | NGP267 | IDMH109860 | NON DG | ID_NAGPUR | 575212 | THAWARE COLONY | NAGPUR | SAI | LEELADHAR BHOSKAR | SMPS | SMPS Obsolute model | Q1 SMPS Replacement planned | Open | 2025-05-15 | 0.5 |  | 0.5 |  | 2
1929 | NIMG01 | IDMH102430 | DG | ID_SATARA | 459643 | NIMGAON | SOLAPUR | SAI | CHANDRAKANT ANGADI | SMPS | SMPS LVD Faulty | Plan for SMPS rectification | Open | 2025-05-07 | 2.5 | 0.5 | 1 |  | 3
1930 | JPHL01 | IDMH103334 | NON DG | ID_AKOLA | 458434 | JANEPHAL | AKOLA | SAI | RANJEET KAPSE | SMPS | SMPS controller faulty | Plan for SMPS rectification | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1931 | SIRR11 | INMH405780 | DG | ID_PUNENORTH | 589489 | Airtel_Shree Heights | PUNE-1 | SAI | HARSHAL MAHAJAN | SMPS | SMPS controller fauly | Rectification planned | Open | 2025-04-20 | 5.5 | 4.5 | 3.5 | 7 | 4
1932 | BHAG01 | IDMH104652 | DG | ID_RAIGARH | 568588 | BHAGAD | PUNE-2 | ATS | AMAY DORUGADE | SMPS | SMPS Backplane faulty | SMPS rectification done | Closed | 2025-02-13 | 3.5 | 1.5 |  |  | 2
1933 | RSNS01 | IDMH103248 | DG | ID_PUNESOUTH | 458972 | RANJANGAON SANDAS | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty, LVD bypassed | Rectification planned | Open | 2025-04-20 | 4 | 0.5 | 1 |  | 3
1934 | VRGN01 | IDMH101207 | DG | ID_AKOLA | 566254 | OPEN PLOT VARANGAON | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Load Segregation | VIL connected to Critical DCDB & Voltage drom From DCDB to RRU > 4 v | ATC to INSTALL NEW dcdb FROM Non critical source & New 40 AMF Req for Automation & VIL to replace cable | Open | 2025-04-20 |  | 0.5 | 0.5 |  | 2
1935 | KAKR01 | IDMH103241 | DG | ID_SOLAPUR | 459360 | KAKRAMBA | SOLAPUR | SAI | ROHIT GHOLAP | SMPS | SMPS Controller faulty | Plan for SMPS Rectification | Open | 2025-05-15 |  | 0.5 | 0.5 |  | 2
1936 | CHKN51 | IDMH107448 | DG | ID_PUNENORTH | 574921 | SAVTA MALI MANDIR | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS controller faulty | SMPS replacement done | Closed | 2025-01-29 | 0.5 |  |  |  | 1
1937 | RSMA01 | IDMH100183 | DG | ID_CHANDRAPUR | 458127 | RISAMA | NAGPUR | SAI | SWAPNASHIL CHAVHAN | Cable | 3-RRU Connected with single cable & drop > 9 V | VIL To Replace Cable | Open | VIL Support Required | 4 | 4.5 | 2.5 |  | 3
1938 | NYPR01 | IDMH104436 | DG | ID_PUNESOUTH | 459737 | NARAYANPUR(PUR) | PUNE-1 | SAI | Vacant Vacant CE Pune-1 | SMPS | SMPS controller & backplane faulty | SMPS rectification done | Closed | 2025-01-30 | 1.5 |  |  |  | 1
1939 | RMBK01 | IDMH102792 | DG | ID_NANDED | 460383 | RAMPURI BK | CH SAMBHAJI NAGAR | PTPL | MORESHWAR GADHE | Cable | DCDB to RRU Underated cable & Voltage drop > 3 V | cable to replace | Open | VIL Support Required | 0.5 | 1 |  |  | 2
1940 | JNTR01 | INMH005280 | DG | ID_NANDED | 460243 | JINTUR | CH SAMBHAJI NAGAR | NonActive | MORESHWAR GADHE | Load Segregation | Baseband at criticle | Criticle to non criticle converted | Closed | 2025-03-16 | 3.5 | 1 | 1 |  | 3
1941 | PNSK04 | IDMH104931 | DG | ID_AHMEDNAGAR | 460122 | KARHE | AHMEDNAGAR | PTPL | SANDEEP WANI | RRU | RRU faulty | RRU replaced | Closed | 2025-03-31 |  | 0.5 |  |  | 1
1942 | PAIT01 | IDMH105138 | DG | ID_PUNENORTH | 459388 | PAIT | PUNE-1 | ATS | SWAPNIL KARAD | SMPS | SMPS BER | Plan for SMPS replacement | Open | 2025-05-30 |  |  | 0.5 |  | 1
1943 | KODE01 | IDMH103909 | DG | ID_NASHIK | 505518 | KOLDE | NASHIK | ATS | NILESH BHAVSAR | SMPS | SMPS controller faulty | SMPS replaced | Reopen | 2025-02-19 | 3.5 | 1.5 |  | 1 | 3
1944 | PUN823 | IDMH106237 | DG | ID_PUNENORTH | 521158 | PIMPLE SAUDAGAR | PUNE-2 | ATS | VIPIN GUPTA | SMPS | SMPS LVD Faulty | SMPS rectification done | Reopen | 2025-03-31 | 1 | 1 |  | 1 | 3
1945 | MI1057 | INMH408435 |  | ID_PUNENORTH | 459349 | TECH CENTRE YERWADA | PUNE-1 | SAI | VIJAY KOLI | SMPS | Controller Faulty Lvd Bypass | SMPS Rectification done | Closed | 2025-03-31 |  | 1 |  |  | 1
1946 | PCRA04 | IDMH110093 | DG | ID_AURANGABAD | 566082 | SINDHI COLONY-PACHORA | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | SMPS | EMERSON PP BER Single LVD | SMPS replacement required | Open | 2025-05-15 | 0.5 | 0.5 |  |  | 2
1947 | DKNI01 | IDMH109897 | DG | ID_NASHIK | 458838 | DHAKANI (EXT RTR) | KOLHAPUR | SSS | VINAYAK KOLEKAR | SMPS | SMPS LVD issue | SMPS LVD Setting done | Closed | 2025-02-28 |  | 0.5 |  |  | 1
1948 | PU1712 | INMH404453 | NON DG | ID_PUNENORTH | 503292 | VISHAL NAGAR_BANER ROAD | PUNE-2 | NonActive |  | Update pending | Update pending | Update pending | Update pending | Update pending | 0.5 |  |  | 1 | 2
1949 | SAVI01 | IDMH106763 | DG | ID_PUNENORTH | 459338 | SAVINDANE | PUNE-1 | SAI | HARSHAL MAHAJAN | SMPS | SMPS Faulty | Plan for SMPS rectification | Open | 2025-04-30 |  |  | 0.5 |  | 1
1950 | PU1701 | INMH400957 | NON DG | ID_PUNESOUTH | 528827 | NYATI ESTATE,MOHAMMAD WADI | PUNE-1 | ATS | Vacant Vacant CE Pune-1 | SMPS | SMPS controller faulty, Zero battery backup | SMPS replaced | Closed | 2025-01-30 | 1 |  |  |  | 1
1951 | BHWL29 | INMHVF4999 | NON DG | ID_AKOLA | 565756 | BHUSAWAL | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | Update pending | Update pending | Update pending | Update pending | Update pending |  |  |  | 2 | 1
1952 | ADWD03 | INMH408112 | DG | ID_AKOLA | 451545 | ADAWAD_VF_HUB | CH SAMBHAJI NAGAR | PTPL | HEMANT RANE | BB | BB Zero. Need BB replacement | Plan for BB upgradation | Open | 2025-05-07 | 3.5 | 4 | 2 | 1 | 4